General Comments:

A) INTRODUCTION

The following procedure is intended to ensure that the quality of constructed product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for all WWTP Inflow Screenings Units Competent personnel shall complete all inspection / construction activities and record all activities on Water Corporation Document

ITP-PC-M WWTP INLET SCREEN for each asset constructed.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and AS/NZS Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_PC_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

* All Pre-Commissioning documents shall contain the following sections (1 – 2) which capture generic asset information

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment (portable vibration monitor and temperature sensor). |
|  | Provision of required test reports and certificates |
|  | Provision of completed construction verification |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning? |  |  |  |  |
| 2 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 3 | Electrical construction and pre-commissioning ITPs complete? |  |  |  |  |
| 4 | Mechanical and electrical site specific pre-requisite ITPs complete? |  |  |  |  |
| 5 | Check installation is correct & complete as per {insert company} O&M {page ref.} |  |  |  |  |
| 6 | Once installation is complete, check band tension as per {insert company} O&M {page ref.} |  |  |  |  |
| 7 | Check gear unit is fitted correctly. |  |  |  |  |
| 8 | Check gear unit solid plugs have been removed from filler points & correct fillers/breathers are fitted. |  |  |  |  |
| 9 | Check gearbox oil levels. |  |  |  |  |
| 10 | Check all tools & loose materials have been removed. |  |  |  |  |
| 11 | Check wash water is available |  |  |  |  |
| 12 | Remove jet pipe end cover plug. Gently start wash water to flush out any debris and prevent blockage of jets. Stop wash water & refit plug. |  |  |  |  |
| 13 | Remove main inspection cover. Start wash water. Check pressure is 2-4b. Check jets are clear with an even spray coverage 10 degrees off pipe centre line. Refit main inspection cover. |  |  |  |  |

*Contents of Section 4 (Inspection) and Section 5 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 4. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| ROTATION |
| 1 | Check bump test has been done & screen rotated in the correct direction and motor shafts rotate freely without rub or noise |  |  |  |  |
| 2 | Remove main inspection cover (note cover has a safety switch which may need over-riding). Man the E-Stop then CAREFULLY run through one complete revolution and check for smooth operation. Note further revolution testing requires adequate water lubrication via wash water or a hose |  |  |  |  |
| ANCILLARY AND TEMPORARY EQUIPMENT |
| 3 | All ancillary systems available and on-line? (eg. Wash press, screw conveyors etc) |  |  |  |  |
| 4 | Temporary instruments (if required) installed? (eg. vibration transducers, current measure etc.) |  |  |  |  |
| CONTROL AND PROTECTION SYSTEMS |
| 5 | All electrical / instrument control and protection systems available and on-line? Check operation of emergency stop. (e.g. motor protection, process control systems) |  |  |  | . |
| 6 | All mechanical / hydraulic control and protection devices available and on-line? (eg. Torque Limit switches) |  |  |  |  |
| 7 | Check overload is set correctly |  |  |  |  |
| 8 | Check {insert company} O&M {page ref.} true power monitor is set correctly. |  |  |  |  |
| 9 | Check operation of all inspection cover safety switches (normally wired as fail safe). |  |  |  |  |
| 10 | Check set up & operation of {insert company} O&M {page ref.} wash water pressure switch. |  |  |  |  |
| ACCESS |
| 11 | Area around fan assembly clean, free of debris and barricaded off from other works (if required)? |  |  |  |  |
| 12 | Emergency stop pushbutton accessible? |  |  |  |  |

| 5. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| FLOW TEST |
| 1 | Check wash water flows whilst the screen runs (in auto). |  |  |  |  |
| 2 | Check operation of {insert company} O&M {page ref.} wash water pressure gauge. |  |  |  |  |
| PERFORMANCE DATA |
| 3 | Check screen faults if wash water pressure is < {set point} for 30s (in auto). |  |  |  |  |
| PERFORMANCE ASSESSMENT |
| POST TEST CHECKS |

Sections 6 & 7 to be retained in all ITPs.

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES

| A1. MECHANICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |
|  |  |  |  | I |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES (cont’d)

| A2. ELECTRICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |