- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate details match penstock specification |  |  |  |  |
| 2 | Confirm that underground penstocks, spindles and actuators are identically numbered. |  |  |  | Verify that a Stainless Steel number tag has been installed to each. |
| 3 | Inspect and confirm penstock actuator type and spindle drive |  |  |  | Actuator: Electric / Manual Spindle drive: Geared / Direct |
| 4 | Confirm penstock seating type and obtain durometer reading |  |  |  | Seating type: Durometer reading: |
| 5 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| 6 | Confirm that any special tools required to operate the penstock have been provided if ordered from the manufacturer |  |  |  |  |
| 7 | Check that penstock frames are clean and are free from any defects resulting from corrosion or any other causes |  |  |  |  |
| 8 | Inspect penstock to ensure equipment is adequately clean |  |  |  |  |
| MATERIALS AND ARRANGEMENT |
| 9 | Verify construction materials (refer to penstock name plate) with specification and relevant drawings |  |  |  |  |
| 10 | Measure length of penstock and verify correct length with manufacturer dimensions or general arrangement drawing(s). |  |  |  | Length: Checked against: MF Dimensions / G.A. Dwg |
| 11 | Confirm details on name plate match specifications |  |  |  | Flange Aust. Standard: Flange Type: Flange Size: Flange Class: |
| 12 | Measure distance from centreline of penstock to top of cap / hand-wheel and verify with specification |  |  |  | Distance(mm): |
| 13 | Inspect Stainless steel welding has been completed to WS-1 |  |  |  |  |
| 14 | Verify passivation of Stainless Steel has bene completed to WS-! |  |  |  |  |
| GEARBOX (If Applicable) |
| 14 | If gearbox is wrapped, check that wrapping and butylmastic paste is securely fastened and that entire gearbox has been wrapped |  |  |  |  |
| 15 | Inspect gearbox cover plate fasteners and ensure they are tight with zero lubrication leakage. Assess where possible if gearbox is wrapped |  |  |  |  |
| 16 | Check that gearbox to penstock body fasteners is secure. Assess where possible if gearbox is wrapped |  |  |  |  |
| 17 | Check that gearbox / handwheel / actuator are located on correct side of penstock as per GA drawings * Gearbox location to be determined by viewing the penstock from upstream to downstream |  |  |  | Gearbox on: RHS / LHS |
| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| 1 | Open and close the penstock via the hand-wheel / cap (request for penstock key) or electric actuator if installed and ensure seating is correct |  |  |  | Penstock fitted with (circle): Handwheel / Cap |
| 2 | Open and close the penstock and ensure direction is correct |  |  |  |  |
| 3 | Confirm that open / close indication is correct |  |  |  |  |
| 4 | Open and close the penstock. Check that penstock opening / closing convention complies with Water Corporation standards (i.e. ACW close, CW open). |  |  |  | Direction of rotation to close: Anti-clockwise Clockwise |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verified construction materials with specification and relevant drawings |  |  |  | Substrate material: |
| 2 | Review surface pre-treatment and/or preparation procedure (circle A1 Surface preparation of steel or cast iron |  |  |  | A1/ OTHER _________________ |
| 3 | Verify coating system and specification ensuring that product is approved for purpose |  |  |  |  |
| 4 | Ensure that surface preparation was acceptable and free from contaminants prior to coating/complies to spec Consider dust and spent abrasive, oil and contamination, flash rusting, slag, porosity, weld spatter, sharp edges, free from laminations, free from burrs etc |  |  |  | Class of surface finish (if known): Profile (if known): Coating application (if known): |
| 5 | Consider if conditions acceptable for testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing |  |  |  | Conditions: |
| 6 | Fully cured coating system should be adherent while in their service condition (Method AS/NZS 3894.9) |  |  |  | Failure force (if known): |
| 7 | Assess degree of cure and hardness of coating is acceptable (method AS 3894.4). Allow sufficient drying and curing of the coating prior conducting testing. The length of time shall be obtained from the coating manufacture. |  |  |  | Method used: |
| 8 | Checked that penstock frames are clean and are free from any defects resulting from corrosion or any other cause |  |  |  |  |
| 9 | Visually inspect surfaces and ensure is adequately clean and dry prior to testing |  |  |  | Method/chemicals used: |
| 10 | Check internal coating type and verify in accordance with relevant specification (circle C2: Epoxy Coating on Steel/Cast Iron |  |  |  | C2 / OTHER _____________ |
| 11 | Visually inspect condition of internal coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 12 | Check external coating type and verify in accordance with relevant specification (circle C2 |  |  |  | C2 / OTHER _____________ |
| 13 | Visually inspect condition of external coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 14 | Calibrate thickness tester to standard of uniform and calibrated thickness, covering appropriate range of film thicknesses to be measured |  |  |  | Method/instrument used: |
| 15 | Visually inspect and measure dry film thickness (DFT) in at least 10 locations on coated surfaces. Record values, ensure compliance with spec and record in table below (note that Flange Thickness is not considered acceptable if not within minimum – maximum range) |
| 16 | Ensure coating fully cured prior continuity testing by checking datasheet for required time to full cure or other appropriate test method |  |  |  | Temp/time: Test method: |
| 17 | Calibrate holiday detector (spark tester) electrode with appropriate volt meter which has been laboratory calibrated within the last 2 years to proposed voltage. Record brand and model of spark tester to be used. |  |  |  | Brand/model used: |
| 18 | Carry out spark test on internal coating in accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 19 | Carry out spark test on external coating accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 20 | Penstock passes continuity testing with zero defects (including pinholes, holidays, cracks and other discontinuities) detected in finished coating for immersed/buried conditions and/or subsequent repairs have been carried out before being placed in service. |  |  |  |  |

| Coating Thickness: | Internal (micrometers): | External (micrometers): | Flange (micrometers ): | Complies with Spec? |
| --- | --- | --- | --- | --- |
| Specified min |  |  |  | N/A |
| Specified max |  |  |  | N/A |
| Measured 1 |  |  |  |  |
| Measured 2 |  |  |  |  |
| Measured 3 |  |  |  |  |
| Measured 4 |  |  |  |  |
| Measured 5 |  |  |  |  |
| Measured 6 |  |  |  |  |
| Measured 7 |  |  |  |  |
| Measured 8 |  |  |  |  |
| Measured 9 |  |  |  |  |
| Measured 10 |  |  |  |  |
| Average |  |  |  |  |
| Note any comment or variation to test procedure that will assist in interpretation of results: |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pretreatment of Surfaces

2 Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

3 Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

4 Method AS 3894.3 refers Determination of Dry Film Thickness

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

# Footnotes

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pre-treatment of Surfaces

Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

Method AS 3894.3 refers Determination of Dry Film Thickness