| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL ARRANGEMENT |
| 1 | Limits of this inspection clearly defined? |  |  |  | Attach a copy of the relevant P&ID and/or GA drawing highlighting the extent of this inspection. Separate verification for each pipework system is recommended |
| 2 | Pipework material correct? |  |  |  |  |
| 3 | Pipework sizes, schedules and lining thicknesses correct? |  |  |  |  |
| 4 | Pressure / temperature rating of installed components correct? (eg. valves, fittings, flowmeters, strainers, etc.) |  |  |  |  |
| 5 | Components installed in correct location and position per P&ID and GA drawings? |  |  |  | Check valves, fittings, pipe specials, supports, restraints, strainers, gauges etc |
| 6 | Vertical pipe legs plumb? |  |  |  |  |
| 7 | Horizontal pipe legs installed with correct fall/slope if applicable? |  |  |  |  |
| 8 | Parallel pipework evenly spaced and visually acceptable? |  |  |  |  |
| 9 | Vents installed at high points? |  |  |  |  |
| 10 | Drains and/or traps installed at low points? |  |  |  |  |
| 11 | Tapping points and instrument root valves positioned correctly? |  |  |  |  |
| 12 | Space between valves adequate to avoid interference (eg. NRV and BFV discs)? |  |  |  |  |
| 13 | Eccentric reducers installed in correct orientation? |  |  |  |  |
| 14 | Relief valves and bursting disc outlets discharge to safe location? |  |  |  |  |
| 15 | Piping components (eg. valves, strainers etc.) positioned for ease of operation and maintenance? |  |  |  |  |
| BOLTED CONNECTIONS |
| 16 | Check that mating flanges are of correct size, type, facing and alignment |  |  |  |  |
| 17 | Verify gasket material, face width and thickness is correct |  |  |  | Material: CMF Elastomeric Face width: Full Narrow Other _____________________ Thickness: _________________mm |
| 18 | Confirm bolt sizes, material and grade are correct |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 19 | Confirm that associated nut grade is correct |  |  |  | Grade: 5 8 Other __________ |
| 20 | Confirm correct protrusion of bolt threads past nut |  |  |  | Protrusion: _____________________ |
| 21 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |
| 22 | Verify bolt torque requirements comply with DS-38. Also verify actual bolt torque applied to each bolt is correct. |  |  |  | DS38 bolt torque: _____________Nm Actual bolt torque: _____________Nm Note for bolting torques for valves and magflowmeters refer to manufacturer’s recommended values. |
| 23 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| 24 | If required by design, verify that flange isolation materials have been installed correctly |  |  |  |  |
| PIPE SUPPORTS AND FLEXIBLE CONNECTIONS |
| 25 | Pipe support spacing correct? (visual check of deflection only) |  |  |  |  |
| 26 | Continuous support provided for small bore thermoplastic piping? |  |  |  |  |
| 27 | Sufficient flexibility built into piping routes to allow for thermal movement? |  |  |  |  |
| 28 | Supports located to eliminate cantilever loads when valves or other components removed? |  |  |  |  |
| 29 | Supports provided adjacent to tanks and pumps to eliminate nozzle loads? |  |  |  |  |
| 30 | Heavy pipe components (eg. valves) supported independently to avoid loads on pipework? |  |  |  |  |
| 31 | Horizontal valve actuators supported independently of valve, if required? |  |  |  |  |
| 32 | Pipe support materials suitable for environment/conditions? |  |  |  |  |
| 33 | Resilient pipe support seat provided for thermoplastic piping? |  |  |  |  |
| 34 | Flexible connections installed for: - isolation of vibrating or pulsing equipment - isolation of equipment which may settle/move over time - thermal expansion / contraction? |  |  |  |  |
| 35 | Thrust blocks installed as per drawings and specifications |  |  |  |  |
| ISOLATING JOINTS (IF REQUIRED FOR PREVENTION OF DISSIMILAR METALS CORROSION OR CATHODIC PROTECTION ISOLATION |
| 36 | Check that correct isolating bolt sleeves and washers have been installed |  |  |  |  |
| 37 | Verify that flange to flange isolation is acceptable |  |  |  |  |
| 38 | Verify that a test post has been installed |  |  |  |  |
| 39 | Confirm if a surge diverter has been installed |  |  |  |  |
| DISMANTLING JOINTS |
| 40 | Tie-bolts installed and tightened? |  |  |  |  |
| 41 | Pipework either side of joint correctly aligned? |  |  |  |  |
| WELDED JOINTS |
| 42 | Appearance of welds visually acceptable? |  |  |  |  |
| 43 | NDE carried out on welds per code and spec. WS-1 requirements? |  |  |  |  |
| 44 | Confirm correct silver solder or brazing alloy used for copper joints and fittings |  |  |  |  |
| THREADED CONNECTIONS |
| 45 | Ensure the threads are correct for sealing against fluid or gas pressure |  |  |  |  |
| 46 | For sealing threads ensure the correct external and internal taper is adopted |  |  |  | Series RC/RP/R/RL to AS 1722.1 |
| 47 | For copper compression cone fittings confirm threads are not cross threaded |  |  |  |  |
| 48 | Confirm that where applicable the correct thread tape or sealant has been used |  |  |  | Ensure tape or sealant does not present risk of blocking filters/strainers |
| THERMOPLASTIC/POLYMER JOINTS |
| 49 | Correct solvent cement used for PVC or ABS piping system joints? |  |  |  |  |
| 50 | Appearance of PE welds visually acceptable and meets WS-1 requirements? |  |  |  |  |
| INSULATION AND DOUBLE CONTAINMENT |
| 51 | Heat tracing installed correctly? |  |  |  |  |
| 52 | Insulation and cladding materials and thicknesses correct? |  |  |  |  |

| 4. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Complete disinfection followed by bacterial testing of the pipework for potable water pipework according to Work Instruction BWW024-1. |  |  |  |  |
| 2 | Complete hydro testing of pipework to the designated design working pressure of the pipeline. |  |  |  | There shall be no visible leaks at bolted, welded or threaded connections and no discernible drop in pressure over a two hour period |
| 3 | Complete NDT testing of welds as required under specification WS-1 |  |  |  |  |

| 5. COATINGS INSPECTION (Corrosion Control) | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that pipework painted external coating is free of damage |  |  |  |  |
| 2 | Check that internal cement mortar lining is repaired around weld bands and is free of excessive cracking |  |  |  |  |
| 3 | Check that buried pipework PE (Sintakote) coating is free of damage |  |  |  |  |
| 4 | Check that buried pipework wrapping at bolted connections is satisfactory is free of damage |  |  |  |  |
| 5 | Correct colour used for pipe contents to AS 2700? |  |  |  |  |
| 6 | Correct contents labels and flow direction fixed to piping? |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |