| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| CALCULATION TABLE (AS2566 M4) |
| --- |
| Complete the following calculations prior to attending site, taking due note of different units used |
| Parameter | Symbol | Formula | Result | Unit |
| Design pressure | Pdesign |  |  | kPa |
| Pipe pressure rating | Ppipe |  |  | kPa |
| Lowest component pressure rating | Pcomp |  |  | kPa |
| Test pressure | Ptest | Determined by testing engineer. Considering the above pressure limits and applicable Australian Standards. |  | kPa |
| Pipe diameter | D | (Note: DN1000 Pipe Equates to 1m pipe Diameter for calcs) |  | m |
| Length of pipe being tested | L | Noting: L is in different denominations of units for Calculations 7 & 12) |  | m / Km |
| Volume of pipe being tested (should not exceed 4000m3) | V | V=π x D²/4 x L (Note L in this calc is in meters) |  | m3 |
| Maximum fill rate | Qfmax | Qfmax = 12.5 x π x D² |  | L/s |
| Design temperature | Tdesign |  |  | °C |
| M2 test duration. This allows temperature of pipe and water to stabilise and dissolved air to exit the system. | tM2 | Duration between 3 and 24 hours is to be specified by the testing engineer. |  | minutes |
| Average test head over pipe length under test | H | *measured |  | m |
| Maximum allowable make-up water as a Flowrate (NOTE: Make-up water is not a leakage allowance; it covers the effects of test head forcing entrapped air into the solution and would be expected to decrease over the test duration; should there be no leaks). | Qmax | Qmax ≤ 0.14LDH Note: L in this calc is in Kilometers |  | L/h (Flowrate) |

| 3. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment (portable pressure monitor). |
|  | Provision of required test reports and certificates |
|  | Provision of completed construction verification |

| 4. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning? |  |  |  |  |
| 2 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 3 | Boundary of test clearly defined? |  |  |  | Attach a marked copy of the system P&ID or GA drawing clearly showing the extent of the pipework pressure test. Separate testing should be undertaken for each system or pressure rating |
| 4 | Confirm a hydrotesting safe work method statement or plan has been established |  |  |  | This should include procedure, P&ID, isolation register, reference to this ITR and prerequisite ITRs, OSH considerations (barricading), operational assistance |
| 5 | Confirm an isolation register for all equipment isolated has been established |  |  |  | Ensure isolation tags are placed on related valves as well information tags on valves that must be left open as well |
| 6 | Pipeline sections tested do not exceed 5km in length or 4000m3 volume |  |  |  |  |
| 7 | Ensure appropriate barricading has been established where applicable |  |  |  | This important particularly for high pressure testing |
| 8 | Electrical construction and pre-commissioning ITRs complete? |  |  |  | Refer to PQR |
| 9 | Mechanical and electrical site specific pre-requisite ITRs complete? |  |  |  | Refer to PQR |
| 10 | All thrust blocks are in place and cement has been allowed to cure for 7 days. |  |  |  |  |

*Contents of Section 4 (Inspection) and Section 5 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 5. PRE-TEST CHECKS INSPECTIONS (M2) | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | All instruments and pressure sensitive equipment removed from test pipework? |  |  |  |  |
| 2 | Number and location of vents and air valves adequate to prevent air pockets? |  |  |  |  |
| 3 | All openings sealed with fittings (eg. blank flanges, screwed plugs) adequate for the test pressure? |  |  |  |  |
| 4 | All pipes and pipe supports adequately supported? |  |  |  |  |
| 5 | All non-return valves, control valves and pressure relief valves removed or gagged, as required? |  |  |  |  |
| 6 | All valves within the test boundary open? |  |  |  |  |
| 7 | Valves closed and/or blank flanges installed at boundary of test? |  |  |  |  |
| 8 | Is the test rig suitable, including a test pump which will not produce surging on Start/Stop? (Positive Displacement pump preferred) |  |  |  |  |
| 9 | Are all test pressure gauges calibrated and is the range appropriate? Note: The test rig shall be a recently calibrated pressure transducer, data logger and check pressure gauge that has a dial of at least 100 mm in diameter and a pressure range that places the TP within the range 35% to 70% of the gauges full scale. The transducer and the check gauge shall read with 5% of each other, if not they should be recalibrated or replaced. |  |  |  | Main Test Gauge Calibration date:________________ Pressure range:________________ Check Gauge Calibration date:________________ Pressure range:_________________ Back-up Gauge Calibration Date:________________ Pressure range:_________________ |
| 10 | Pressure gauges installed at required locations? 1 – near pump discharge 2 – At lowest point in the system 3 – At highest point in the system |  |  |  | RL: RL: RL: |

| 6. PRE-TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that all air valves are operating correctly and are not isolated |  |  |  |  |
| 2 | Slowly fill the pipe with water from the lowest point possible. Fill at a rate below Qfmax (ref. Calculation 8) NOTE: Do not pressurise the system |  |  |  |  |
| 3 | Isolate all air valves once all air has been purged from the system |  |  |  |  |
| 4 | Following completion of the Test Duration tM2 (ref. Calculation 10) measure water and ambient air temperature and record. |  |  |  | Start time: Finish time: TAIR: TWATER: |
| 5 | Does the pipe appear to be holding water? Any signs indicating loss of water must be investigated before proceeding. |  |  |  |  |

Note: For cement-mortar lined pipe, the pre-test shall be carried out at least 24 h before the commencement of the constant pressure test, to allow the lining to become saturated.

| 7. CONSTANT PRESSURE TEST (M4) | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Purge all air from the pipeline |  |  |  |  |
| 2 | Raise pressure to Ptest (ref. Calculation 4) |  |  |  |  |
| 3 | Maintain test pressure by the addition of measured and recorded quantities of make-up water at regular intervals over a period, within the range of 1 h to 12 h. |  |  |  |  |
| 4 | Conclude testing if the amount of require make-up water used in an hour period exceeds the maximum allowable quantity of make-up water. |  |  |  |  |
| 5 | Test can be concluded if pressure remains constant over a period of 1h. |  |  |  |  |
| 4 | Was there any failure of any thrust block, pipe, fitting, joint or any other pipeline component |  |  |  |  |
| RESULTS |  |
| Hour | Pressure (kPA) | Make Up Water Used (L) | Water Temperature (°C) | Ambient Temperature (°C) | Comments |
| 0 | PTest= | 0 |  |  |  |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| 11 |  |  |  |  |  |
| 12 |  |  |  |  |  |
| 8. POST TEST |
| 1 | Safely depressurize system and confirm the system is depressurized. |  |  |  |  |
| 2 | Has the test fluid been disposed of appropriately? |  |  |  | Refer to Work Instruction BWW024-2 for disposal of test water. Note if disinfection is required the test water can be used for this purpose and hence should not be drained |
| 3 | Pipework dried and sealed (if required)? |  |  |  |  |
| 4 | Is disinfection and disposal required? |  |  |  | Refer to Work Instruction BWW024-1 |

| 9. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 10. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |