| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

*Contents of Section 3 (Inspection) and Section 4 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that pipework label details match specification and contract requirements |  |  |  | Check: Design Standard/Nominal Bore Diameter/Design Pressure/Type of Fluid/Max Surge Pressure |
| 2 | Confirm if datasheets have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| MATERIALS AND ARRANGEMENT |
| 3 | Verify construction materials with material certs, specification and relevant drawings |  |  |  | Check: Material Type/Grade/Standard |
| 4 | Confirm major key dimensions correct per drawing |  |  |  | Attach a copy of the pipework drawing to this record sheet highlighting on the drawing which dimensions were checked. |
| 5 | Verify that all welds meet WS-1 requirements |  |  |  | Ensure a welding consultant is engaged and all associated welding documents are obtained |
|  | Pipes |  |  |  |  |
| 6 | External coating meets specification? |  |  |  | Coating Type: Sintakote/Painted |
| 7 | Check material for suitability for fluid or gas characteristics |  |  |  | Check suitability on the basis of: Corrosivity Temperature Hazard level of fluid/gas Water quality issues |
| 8 | Check material for suitability for environmental conditions |  |  |  | Check suitability on the basis of: Above Ground or Buried Soil corrosivity Exposure to sunlight Dissimilar metal corrosion |
| 9 | For carbon steel pipe confirm it is seamless or electric resistance welded (ERW) |  |  |  |  |
| 10 | For cement mortar lined piping (MSCL or CML) confirm the uniformity and thickness of lining meets WC specifications |  |  |  | Thickness:…………mm |
| 11 | Confirm the cement lining is profiled to match any machinery interface such as pump suction nozzles |  |  |  |  |
| 12 | Confirm the cement lining is free of excessive cracking and porosity especially around tapping points |  |  |  |  |
| 13 | For H2S attack prone application is the cement lining coated to prevent corrosion |  |  |  |  |
| 14 | Confirm cement lining will not interfere with operation of valves |  |  |  |  |
| 15 | Check tapping points are located correctly and plugs are installed were applicable |  |  |  | Ensure air venting points are located at the highest locations |
| 16 | Confirm earthing studs are fitted |  |  |  |  |
| 17 | Ensure anode brackets and ribbons are fitted and secure |  |  |  |  |
| 18 | Temporary internal bracing installed for transport if applicable? |  |  |  | Applicable to large diameter thin walled MSCL pipework |
| 19 | For Polymer based pipes check for external cracking, kinks and sun-damage |  |  |  | Applicable to: HDPE/PE/PVC-O/PVC-M/PVC-U/ABS Note pipe maybe supplied on a reel which will require unrolling to allow thorough inspection |
| 20 | For ABS and PVC-U/M, confirm the pipework is not subject to cyclic loading such as those related to multiple pump starts/stop and valve opening/closing |  |  |  |  |
| 21 | Ensure where ABS joins to PVC piping that the solvent cement is compatible to both materials |  |  |  |  |
| 22 | Confirm PVC-U is not being used on compressed air lines |  |  |  |  |
| 23 | For copper pipe check for signs of work hardening, kinks and zincification |  |  |  |  |
| 24 | For copper confirm the pipe is designed to accommodate capillary or compression cone fittings |  |  |  |  |
| 25 | For galvanise steel confirm pipe has been hot dipped galvanised |  |  |  |  |
| 26 | For GRP piping confirm the nominal stiffness (SN) is 5000 or greater |  |  |  |  |
| 27 | For buried ductile iron (DI) pipe confirm internals are CML and external is cold applied bituminous paint (short term) and external polyethylene sleeve (long term) |  |  |  |  |
| 28 | For polyethylene pipe (PE) ensure it is either medium or high density with a PN12.5 or greater rating |  |  |  | Note the colour and striping of the pipe for identification |
| 29 | For stainless steel pipe (SS) confirm the schedule is 10S or greater and low grade carbon content when welding is required |  |  |  |  |
| 30 | For spiral welded (SS) pipe confirm this has been TIG welded and used only up to 75mm pipe |  |  |  |  |
| 31 | Confirm stainless steel pipework has been pickled and passivated |  |  |  |  |
| 32 | Confirm end connections are correct to suit fittings |  |  |  | Threaded/Flanged/Victaulic/Welded/ /Compression/Camlock/Bevelled/Elastomeric Seal Joint/Solvent Cement Welding/ Rubber Ring joints |
|  | Flanges |  |  |  |  |
| 33 | Confirm flange standard correct |  |  |  | Design Standard: AS……../EN…….…. |
| 34 | Check flange type is correct |  |  |  | Weldneck/Plate/Slip-On/Threaded/Loose/Socket Weld/Blind |
| 35 | Ensure flange facing and finish is correct |  |  |  | Raised/Flat |
| 36 | Check flange thickness is correct |  |  |  | Thickness: ……..mm |
| 37 | Confirm outside diameter is correct |  |  |  | Class: |
| 38 | Confirm pitch circle diameter is correct |  |  |  | PCD: _____________ mm |
| 39 | Ensure number and diameter of drilled bolt holes are correct |  |  |  | No.:______ Dia.:________ mm |
| 40 | Check number and diameter of threaded bolt holes are correct |  |  |  | No.:______ Dia.:________ mm |
| 41 | Check threads on holes are free of defects |  |  |  | Use GO/NO-GO gauge if applicable |
| 42 | Confirm spot facing on bolt head landings |  |  |  |  |
|  | Elbows/Bends/Tees/Reducers/Strainers |  |  |  |  |
| 43 | Confirm end connection correct? |  |  |  | Threaded/Flanged/Victaulic /Compression/Camlock |
| 44 | Diameter correct? |  |  |  | DN_____mm |
| 45 | Angle of fitting correct? |  |  |  | Degrees:___ |
| 46 | Aperture of strainers correct to suit process fluid expected filtrate? |  |  |  | Aperture: ____ mm |
|  | Pipe Supports/Restraints |  |  |  |  |
| 47 | Confirm support/restraint type is suitable for intended pipe |  |  |  | Fabricated/Clamp Stye/Free-sliding/ |
| 48 | Confirm fabricated support/restraint key dimensions are correct |  |  |  |  |
| 49 | For “off the shelf” supports check details match drawings and specification |  |  |  | These may include Binder engineered supports |
| 50 | Confirm mounting baseplate matches drawings and specification |  |  |  |  |
| 51 | Check mounting baseplate squareness relative pipe centreline and mounting surface |  |  |  |  |
| 52 | Confirm pipe supports for stainless steel pipe is made of either stainless or hot dipped galvanised |  |  |  |  |
|  | Pipe Specials/Flange Matching Piece |  |  |  |  |
| 53 | Confirm pipe special’s dimensions are correct |  |  |  |  |
| 54 | Check end connection details are correct |  |  |  | Threaded/Flanged/Victaulic /Compression/Camlock/Bevelled |
| 55 | Confirm flange detail is correct in-line with previous checklist items above |  |  |  |  |
| 56 | Confirm cement motor lining meets WC standards |  |  |  |  |
| 57 | Lifting eyes/lugs correctly located and fitted or welded? |  |  |  | Ensure a welding consultant is engaged and all associated welding documents are obtained |
| 58 | Anode brackets and ribbons fitted and secure? |  |  |  |  |
| 59 | Confirm crotch plate detail is correct |  |  |  |  |
|  | Joints and Fittings |  |  |  |  |
| 60 | For copper pipe confirm the fittings are either capilliary or compression cone type |  |  |  |  |
| 61 | For copper capilliary long engagement sockets, silver solder shall be used |  |  |  |  |
| 62 | For copper capilliary short engagement sockets, brazing alloy shall be used |  |  |  |  |
| 63 | For ABS pipe joints confirm the use of solvent cleaner and cement shall be used |  |  |  |  |
| 64 | For duct iron pipe confirm the use of flanged or socketed joints |  |  |  |  |
| 65 | For MSCL pipework confirm welded bands provided meet WC specifications |  |  |  |  |
| 66 | For stainless steel (SS), fittings should be screwed |  |  |  | Low Pressure Male: BSPT-R series Female: BSPP –RP series High Pressure NPT |
|  | Gasketing |  |  |  |  |
| 67 | Confirm compressed fibre gasket are utlised in-lieu of o-rings and reinforced fabric gaskets |  |  |  |  |
| 68 | For compressed fibre gaskets confirm thickness is as specified |  |  |  | Thickness normally 1.5mm to 3mm |
| 69 | Where natural rubber or EPDM is being used confirm hydrocarbons are not present in the gas or liquid |  |  |  | Use NBR in high hydrocarbon applications |
| 70 | Confirm for gaseous chlorine and chlorine solution lines that gaskets are made of FPM (Viton) |  |  |  |  |
| 71 | Confirm the gasket is correctly full or narrow faced to suit pressure rating and pipework size |  |  |  |  |

| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Confirm Material certificates are acceptable |  |  |  |  |
| 2 | Confirm welding documentation (incl NDT) are acceptable |  |  |  |  |
| 3 | Confirm heat treatment certificates are acceptable |  |  |  |  |
| 4 | Confirm pickling and passivation evidence documentation is acceptable for stainless steel |  |  |  |  |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6-9 to be retained in all ITPs.

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verified construction materials with specification and relevant drawings |  |  |  | Substrate material: |
| 2 | Review surface pre-treatment and/or preparation procedure (circle PH: Epoxy Coating on Steel/Cast Iron or state Other) |  |  |  | PA / OTHER _________________ |
| 3 | Verify coating system and specification ensuring that product is approved for purpose |  |  |  |  |
| 4 | Ensure that surface preparation was acceptable and free from contaminants prior to coating/complies to spec Consider dust and spent abrasive, oil and contamination, flash rusting, slag, porosity, weld spatter, sharp edges, free from laminations, free from burrs etc |  |  |  | Class of surface finish (if known): Profile (if known): Coating application (if known): |
| 5 | Consider if conditions acceptable for testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing |  |  |  | Conditions: |
| 6 | Fully cured coating system should be adherent while in their service condition (Method AS/NZS 3894.9) |  |  |  | Failure force (if known): |
| 7 | Assess degree of cure and hardness of coating is acceptable (method AS 3894.4). Allow sufficient drying and curing of the coating prior conducting testing. The length of time shall be obtained from the coating manufacture. |  |  |  | Method used: |
| 8 | Checked that flange faces are clean and are free from any defects resulting from corrosion or any other cause |  |  |  |  |
| 9 | Visually inspect surfaces and ensure is adequately clean and dry prior to testing |  |  |  | Method/chemicals used: |
| 10 | Check internal coating type and verify in accordance with relevant specification (circle PH: Epoxy Coating on Steel/Cast Iron or state, PA: Protective Coating on Steel/Cast Iron or state Other) |  |  |  | PA / PH / OTHER _____________ |
| 11 | Visually inspect condition of internal coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 12 | Check external coating type and verify in accordance with relevant specification (circle PH: Epoxy Coating on Steel/Cast Iron or state, PA: Protective Coating on Steel/Cast Iron or state, PS: Inorganic zinc silicate primed two pack acrylic coating or Other ) |  |  |  | PA / PH / PS/ OTHER _____________ |
| 13 | Visually inspect condition of external coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 14 | Calibrate thickness tester to standard of uniform and calibrated thickness, covering appropriate range of film thicknesses to be measured |  |  |  | Method/instrument used: |
| 15 | Visually inspect and measure dry film thickness (DFT) in at least 10 locations on coated surfaces. Record values, ensure compliance with spec and record in table below (note that Flange Thickness is not considered acceptable if not within minimum – maximum range) |
| 16 | Ensure coating fully cured prior continuity testing by checking datasheet for required time to full cure or other appropriate test method |  |  |  | Temp/time: Test method: |
| 17 | Calibrate holiday detector (spark tester) electrode with appropriate volt meter which has been laboratory calibrated within the last 2 years to proposed voltage. Record brand and model of spark tester to be used. |  |  |  | Brand/model used: |
| 18 | Carry out spark test on internal coating in accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 19 | Carry out spark test on external coating accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 20 | Asset passes continuity testing with zero defects (including pinholes, holidays, cracks and other discontinuities) detected in finished coating for immersed/buried conditions and/or subsequent repairs have been carried out before being placed in service. |  |  |  |  |

| Coating Thickness: | Internal (micrometers): | External (micrometers): | Flange (micrometers ): | Complies with Spec? |
| --- | --- | --- | --- | --- |
| Specified min |  |  |  | N/A |
| Specified max |  |  |  | N/A |
| Measured 1 |  |  |  |  |
| Measured 2 |  |  |  |  |
| Measured 3 |  |  |  |  |
| Measured 4 |  |  |  |  |
| Measured 5 |  |  |  |  |
| Measured 6 |  |  |  |  |
| Measured 7 |  |  |  |  |
| Measured 8 |  |  |  |  |
| Measured 9 |  |  |  |  |
| Measured 10 |  |  |  |  |
| Average |  |  |  |  |
| Note any comment or variation to test procedure that will assist in interpretation of results: |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pre-treatment of Surfaces

2 Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

3 Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

4 Method AS 3894.3 refers Determination of Dry Film Thickness

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

# Footnotes

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pretreatment of Surfaces

Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

Method AS 3894.3 refers Determination of Dry Film Thickness