| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| CALCULATION TABLE (AS2566 M5) |
| --- |
| Complete the following calculations prior to attending site |
| Parameter | Symbol | Formula | Result | Unit |
| Design pressure | Pdesign |  |  | kPa |
| Pipe pressure rating | Ppipe |  |  | kPa |
| Lowest component pressure rating | Pcomp |  |  | kPa |
| Test pressure | Ptest | Determined by testing engineer. Considering the above pressure limits and applicable Australian Standards. |  | kPa |
| Pipe diameter | D | (Note: DN1000 Pipe Equates to 1m pipe Diameter for calcs) |  | m |
| Length of pipe being tested | L | Noting: L is in different denominations of units for Calculations 7 & 14) |  | m / Km |
| Volume of pipe being tested (should not exceed 4000m3) | V | V=π x D²/4 x L (Note L in this calc is in meters) |  | m3 |
| Maximum fill rate | Qfmax | Qfmax = 12.5 x π x D² |  | L/s |
| Design temperature | Tdesign |  |  | °C |
| M2 test duration. This allows temperature of pipe and water to stabilise and dissolved air to exit the system. | tM2 | Duration between 3 and 24 hours is to be specified by the testing engineer. |  | minutes |
| Average test head over pipe length under test | H | *measured |  | m |
| 1st Volume Added (Note: V1 is the volume of water required to maintain the test pressure constant between Hour 2 and Hour 3) | V1 | *measured |  | L (Litres) (Volume) |
| 2nd Volume Added (Note: V2 is the volume of water required to maintain the test pressure constant between Hour 4 and Hour 5) | V2 | *measured |  | L (Litres) (Volume) |
| Maximum allowable make-up water NOTE 1: this calculation must be performed on site once V1 is determined (Make-up water is not a leakage allowance; it covers the effects of test head forcing entrapped air into the solution and would be expected to decrease over the test duration; should there be no leaks). | V2max | ≤ 0.55V1 + 0.14LDH Note: L in this calc is in Kilometers |  | L (Litres) (Volume) |

| INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment (portable pressure monitor). |
|  | Provision of required test reports and certificates |
|  | Provision of completed construction verification |

| INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of any significant defects which could prevent pre-commissioning? |  |  |  |  |
| 2 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 3 | Boundary of test clearly defined? |  |  |  | Attach a marked copy of the system P&ID or GA drawing clearly showing the extent of the pipework pressure test. Separate testing should be undertaken for each system or pressure rating |
| 4 | Confirm a hydrotesting safe work method statement or plan has been established |  |  |  | This should include procedure, P&ID, isolation register, reference to this ITR and prerequisite ITRs, OSH considerations (barricading), operational assistance |
| 5 | Confirm an isolation plan has been established |  |  |  | Ensure isolation tags are placed on all equipment which forms part of the isolation |
| 6 | The pipeline sections to be tested do not exceed 5km in length or 4000m3 in volume. |  |  |  |  |
| 7 | Ensure appropriate barricading has been established where applicable |  |  |  | This important particularly for high pressure testing |
| 8 | Electrical construction and pre-commissioning ITRs complete? |  |  |  | Refer to PQR |
| 9 | Mechanical and electrical site specific pre-requisite ITRs complete? |  |  |  | Refer to PQR |
| 10 | All thrust blocks are in place and cement has been allowed to cure for 7 days. |  |  |  |  |

| INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| PRE-TEST CHECKS |
| 1 | All instruments and pressure sensitive equipment removed from test pipework? |  |  |  |  |
| 2 | Number and location of vents and air valves adequate to prevent air pockets? |  |  |  |  |
| 3 | All openings sealed with fittings (eg. blank flanges, screwed plugs) adequate for the test pressure? |  |  |  |  |
| 4 | All pipes and pipe supports adequately secured? |  |  |  |  |
| 5 | All non-return valves, control valves and pressure relief valves removed or held open? |  |  |  |  |
| 6 | All valves within the test boundary open? |  |  |  |  |
| 7 | Valves closed and/or blank flanges installed at boundary of test? |  |  |  |  |
| 8 | Is the test rig suitable, including a test pump which will not produce surging on Start/Stop? (Positive Displacement pump preferred) |  |  |  |  |
| 9 | Are all test pressure gauges calibrated and is the range appropriate? Note: The test rig shall be a recently calibrated pressure transducer, data logger and check pressure gauge that has a dial of at least 100 mm diameter and a pressure range that places the TP within the range 35% to 70% of the gauge’s full scale. The transducer and the check gauge shall read within 5% of each other, if not they should be re-calibrated or replaced. |  |  |  | Main Test Gauge Calibration date: _____________ Pressure range: _____________ Back-up Gauge Calibration date: _____________ Pressure range: _____________ Back-up Gauge Calibration date: _____________ Pressure range: _____________ |
| 10 | Pressure gauges installed at required locations? 1 – near pump discharge 2 – At lowest point in system 3 – At highest point in system |  |  |  | RL: RL: RL: |

| PRE-TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that all air valves are operating correctly and are not isolated. |  |  |  |  |
| 2 | Slowly fill the pipe with water from the lowest point possible. Fill at a rate below Qfmax (ref. Calculation 8). NOTE: Do not pressurise the system |  |  |  |  |
| 3 | Isolate all air valves once all air has been purged from the system. |  |  |  |  |
| 4 | Following completion of the Test Duration tM2 (ref. Calculation 10) measure water and ambient air temperature and record. |  |  |  | Start time: Finish time: TAIR: TWATER: |
| 5 | Does the pipe appear to be holding water? Any signs indicating loss of water must be investigated before proceeding. |  |  |  |  |

| CONSTANT PRESSURE TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Purge all air from the pipeline |  |  |  |  |
| 2 | Raise pressure to Ptest (ref. Calculation 4) |  |  |  |  |
| 3 | Isolate and allow to settle for 12 hours (the pressure will drop significantly) |  |  |  | Start date / time: Finish date / time: |
| 4 | Reapply pressure Ptest (ref. Calculation 4) and maintain by pumping continuously or at regular intervals such that the pressure does not fall significantly below Ptest NOTE: DO NOT EXCEED Ptest |  |  |  | Start time: |
| 5 | Measure and record water volume added between hours 2-3 to maintain the pressure (V1). Use V1 to calculate V2max (ref. Calculation 14) |  |  |  | V1: L |
| 6 | Measure and record water volume added between hours 4-5 to maintain the pressure (V2) |  |  |  | V2: L |
| 7 | If V2 less than V2max (ref. Calculation 14) pipework system PASSES. If V2 is greater than V2max the pipe must be investigated for leaks and re-tested. |  |  |  |  |
| POST TEST |
| 1 | Pressure gauge returns to zero after pipework system has been de-pressurised? |  |  |  |  |
| 2 | Test fluid disposed of appropriately? |  |  |  | Refer to Work Instruction BWW024-2 for disposal of test water. Note if disinfection is required the test water can be used for this purpose and hence should not be drained |
| 3 | Pipework dried and sealed (if required)? |  |  |  |  |
| DISINFECTION & DISPOSAL |
| 4 | Ensure pipework is filled with disinfection water according to relevant work instruction |  |  |  | Refer to Work Instruction BWW024-1. |
| 5 | Ensure access is made available for bacterial testing |  |  |  | Refer to “Pre-commissioning Quality Check Form” in Work Instruction BWW024-1 |
| 6 | Ensure provision of the sampling point or the removal of an air valve for access by the sampler |  |  |  | Note sampling and testing to be undertaken Manual SG074. |
| 7 | Confirm acceptance of bacterial test results |  |  |  | Acceptance is obtained from Metropolitan Water Quality Coordinator (or equivalent in country regions) |
| 8 | Confirm that the Disinfection Water Disposal Plan and Record Form is completed correctly |  |  |  | Refer to Work Instruction BWW024-2 for disposal of disinfection water. Ensure Disposal Plan has been developed to BWW024-2. |
| 9 | Ensure communication with DPaW and other authorities during disposal is maintained |  |  |  |  |
| 10 | Ensure that monitoring results prior and during disposal of disinfection water are correctly registered |  |  |  |  |
| 11 | Disinfection water disposed of appropriately? |  |  |  |  |

| REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |