A) INTRODUCTION

The following procedure is intended to ensure that the quality of constructed product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for all HEAT EXCHANGER. Competent personnel shall complete all inspection / construction activities and record all activities on Water Corporation Document ITP-CV-M-HEAT EXCHANGER PLATE for each asset constructed.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and AS/NZS Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_CV_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Visually inspect heat exchanger installation and verify correct installation as per manufacturer’s recommendations |  |  |  |  |
| 2 | Confirm that heat exchanger location is correct as per drawings |  |  |  |  |
| 3 | Cold fluid in and out pipework connected to the correct port |  |  |  |  |
| 4 | Hot fluid in and out pipework connected to the correct port |  |  |  |  |
| 5 | Check that mating flanges are flat, clean and free of irregularities |  |  |  |  |
| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| 6 | Confirm that flow plates are free from defects/distortion and no visible signs of plate gasket damage |  |  |  |  |
| 7 | Confirm all tie bar, connecting pipework and top/bottom bar bolts installed on heat exchanger and that bolt sizes, material and grade are correct |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 8 | Confirm that associated tie bar, connecting pipework and top/bottom bar nut grade is correct |  |  |  | Grade: 5 8 Other __________ |
| 9 | Confirm the tie bar bolts have been tightened such that the dimension between head and follower results in the correct compression of plate pack gaskets. Refer to nameplate or manufacturers assembly drawing. |  |  |  | Manufacturers often specify a minimum and maximum compressed dimension |
| 10 | Confirm correct protrusion of all bolt threads past nut |  |  |  | Protrusion: _____________________ |
| 11 | Confirm correct bolt tightening sequence has been followed for connecting pipework |  |  |  |  |
| 12 | Verify manufacturers bolt torque requirements comply with DS-38. Also verify actual bolt torque applied to each bolt is correct |  |  |  | DS38 bolt torque: _____________Nm Actual bolt torque: _____________Nm |
| 13 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| 14 | If required by design, verify that flange isolation materials have been installed correctly |  |  |  |  |
| 15 | Ensure heat exchanger is level. If not shim/pack the feet. |  |  |  |  |
| 16 | Ensure mounting feet holding down bolts are torqued correctly |  |  |  |  |
| 17 | Check if a dividing plate is installed in the correct position if applicable |  |  |  |  |
| 18 | Ensure any sections of tie bar bolts protruding through follower is not presenting a risk to personnel. Place a plastic cover over end of bar if necessary. |  |  |  |  |
| 19 | Ensure any unused ports or threaded holes are covered. |  |  |  |  |
| ISOLATING JOINTS (IF REQUIRED FOR DISSIMILAR METALS OR CATHODIC PROTECTION ISOLATION) |
| 19 | Check that correct isolating bolt sleeves and washers have been installed |  |  |  |  |
| 20 | Verify that flange to flange isolation is acceptable |  |  |  |  |

| 4. TEST | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| Not applicable |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that valve external coating is free of damage. Touch-up coatings to manufacturer’s recommendations if applicable. |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |