* Sections A & B shall be retained in all ITPs to maintain consistency and when saving documents in AQUA.

A) INTRODUCTION

The following procedure is intended to ensure that the quality of procured product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for all HEAT EXCHANGERS - PLATE. Competent personnel shall complete all inspection / construction activities and record all activities on Water Corporation Document ITP-SV-M-HEAT EXCHANGER-PLATE for each asset Inspected.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and Australian Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_SV_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

* All Supply Verification documents shall contain the following sections (1 – 3) which capture generic asset information

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate/label details match specification or drawings |  |  |  | Check the following Flow rate/Cooling Capacity/TagNumber/Number of Plates/Design Pressure |
| 2 | Confirm tie-bar fasteners/nuts are secure and tightened correctly |  |  |  |  |
| 3 | Ensure flange mating faces are free of surface damage and misalignment |  |  |  |  |
| 4 | Confirm cooling plates are free of damage and misalignment and secure |  |  |  |  |
| 5 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| MATERIALS AND ARRANGEMENT |
| 6 | Verify construction materials with specification and relevant drawings |  |  |  |  |
| 7 | Confirm overall dimensions are correct |  |  |  | Checked against: MF Dimensions / G.A. Dwg |
| 8 | Confirm flange details match specifications or drawings |  |  |  | Flange Aust/International Standard: Flange Type: Flange Size: Flange Class: |
| 9 | Measure pitch circle diameter of flange connections and verify with specification / relevant Standards |  |  |  | PCD: |
| 10 | Count number of flange studbolts and measure diameters. Verify number and diameter with specification / relevant Standards |  |  |  | No.: Dia: |
| 11 | Confirm primary and secondary inlet and outlets relative positions match specifications and drawings |  |  |  |  |
| 12 | Confirm mounting plates are positioned and dimensionally correct |  |  |  | Checked against: MF Dimensions / G.A. Dwg |

| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Confirm the heat exchanger has passed pressure testing requirements by reviewing pressure certificates |  |  |  |  |
| 2 | Confirm material certificates correlate with specifications or drawings |  |  |  |  |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6-9 to be retained in all ITPs.

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verified construction materials with specification and relevant drawings |  |  |  | Substrate material: |
| 2 | Review surface pre-treatment and/or preparation procedure (circle PH: Epoxy Coating on Steel/Cast Iron or state Other) |  |  |  | PA / OTHER _________________ |
| 3 | Verify coating system and specification ensuring that product is approved for purpose |  |  |  |  |
| 4 | Ensure that surface preparation was acceptable and free from contaminants prior to coating/complies to spec Consider dust and spent abrasive, oil and contamination, flash rusting, slag, porosity, weld spatter, sharp edges, free from laminations, free from burrs etc |  |  |  | Class of surface finish (if known): Profile (if known): Coating application (if known): |
| 5 | Consider if conditions acceptable for testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing |  |  |  | Conditions: |
| 6 | Fully cured coating system should be adherent while in their service condition (Method AS/NZS 3894.9) |  |  |  | Failure force (if known): |
| 7 | Assess degree of cure and hardness of coating is acceptable (method AS 3894.4). Allow sufficient drying and curing of the coating prior conducting testing. The length of time shall be obtained from the coating manufacture. |  |  |  | Method used: |
| 8 | Checked that flange faces are clean and are free from any defects resulting from corrosion or any other cause |  |  |  |  |
| 9 | Visually inspect surfaces and ensure is adequately clean and dry prior to testing |  |  |  | Method/chemicals used: |
| 10 | Check internal coating type and verify in accordance with relevant specification (circle PH: Epoxy Coating on Steel/Cast Iron or state, PA: Protective Coating on Steel/Cast Iron or state Other) |  |  |  | PA / PH / OTHER _____________ |
| 11 | Visually inspect condition of internal coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 12 | Check external coating type and verify in accordance with relevant specification (circle PH: Epoxy Coating on Steel/Cast Iron or state, PA: Protective Coating on Steel/Cast Iron or state Other ) |  |  |  | PA / PH / OTHER _____________ |
| 13 | Visually inspect condition of external coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 14 | Calibrate thickness tester to standard of uniform and calibrated thickness, covering appropriate range of film thicknesses to be measured |  |  |  | Method/instrument used: |
| 15 | Visually inspect and measure dry film thickness (DFT) in at least 10 locations on coated surfaces. Record values, ensure compliance with spec and record in table below (note that Flange Thickness is not considered acceptable if not within minimum – maximum range) |
| 16 | Ensure coating fully cured prior continuity testing by checking datasheet for required time to full cure or other appropriate test method |  |  |  | Temp/time: Test method: |
| 17 | Calibrate holiday detector (spark tester) electrode with appropriate volt meter which has been laboratory calibrated within the last 2 years to proposed voltage. Record brand and model of spark tester to be used. |  |  |  | Brand/model used: |
| 18 | Carry out spark test on internal coating in accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 19 | Carry out spark test on external coating accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 20 | Valve passes continuity testing with zero defects (including pinholes, holidays, cracks and other discontinuities) detected in finished coating for immersed/buried conditions and/or subsequent repairs have been carried out before being placed in service. |  |  |  |  |

| Coating Thickness: | Internal (micrometers): | External (micrometers): | Flange (micrometers ): | Complies with Spec? |
| --- | --- | --- | --- | --- |
| Specified min |  |  |  | N/A |
| Specified max |  |  |  | N/A |
| Measured 1 |  |  |  |  |
| Measured 2 |  |  |  |  |
| Measured 3 |  |  |  |  |
| Measured 4 |  |  |  |  |
| Measured 5 |  |  |  |  |
| Measured 6 |  |  |  |  |
| Measured 7 |  |  |  |  |
| Measured 8 |  |  |  |  |
| Measured 9 |  |  |  |  |
| Measured 10 |  |  |  |  |
| Average |  |  |  |  |
| Note any comment or variation to test procedure that will assist in interpretation of results: |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pretreatment of Surfaces

2 Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

3 Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

4 Method AS 3894.3 refers Determination of Dry Film Thickness

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

# Footnotes

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pretreatment of Surfaces

Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

Method AS 3894.3 refers Determination of Dry Film Thickness