A) INTRODUCTION

The following procedure is intended to ensure that the quality of constructed product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for all REGULATING VALVE SLEEVE Competent personnel shall complete all inspection / construction activities and record all activities on Water Corporation Document ITP-PC-M-VALVE-REGULATING-SLEEVE for each asset constructed.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and AS/NZS Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_PC_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

* All Pre-Commissioning documents shall contain the following sections (1 – 2) which capture generic asset information

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |
|  | Provision of completed construction verification |

| 3. INSPECTION PRELIMINARIES | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | “Punchlist” reviewed and free of significant defects preventing asset pre-commissioning? |  |  |  |  |
| 2 | Hazard identification and risk assessment for asset pre-commissioning complete? |  |  |  |  |
| 3 | Electrical construction and pre-commissioning ITPs complete? |  |  |  |  |
| 4 | Mechanical and electrical site specific pre-requisite ITPs complete? |  |  |  |  |

*Contents of Section 4 (Inspection) and Section 5 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 4. INSPECTION & TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| MANUAL OPERATION - APPLIES TO MANUAL VALVES AND MANUAL OVERIDE OF ELECTRICALLY ACTUATED VALVES (NB: Check with manufacturer prior to operating valve “dry”). |
| 1 | Valve operates smoothly throughout valve range during opening? |  |  |  |  |
| 2 | Handwheel rim force acceptable during opening? |  |  |  |  |
| 3 | Open position indication correct? |  |  |  |  |
| 4 | Valve operates smoothly throughout valve range during closing? |  |  |  |  |
| 5 | Handwheel rim force acceptable during closing? |  |  |  |  |
| 6 | Handwheel direction of rotation to close correct for valve type? |  |  |  | Direction of rotation to close: Anti-clockwise Clockwise |
| 7 | Number of turns to close acceptable? |  |  |  | Number of turns to close: ____________ |
| 8 | Close position indication correct? |  |  |  |  |
| ELECTRIC ACTUATOR (TO BE COMPLETED WITH COMPETENT ELECTRICAL PERSONNEL) (NB: Check with manufacturer prior to operating valve “dry”). |
| Direction of Rotation Set-Up |
| 9 | Actuator direction of rotation to close set correctly to match valve? |  |  |  |  |
| Travel Limits Set-Up |
| 10 | Open travel limit type correct for valve type? |  |  |  | Open limit type: Position Torque |
| 11 | Open travel limit set correctly? |  |  |  | Torque limit (if applicable): _________Nm |
| 12 | Close travel limit type correct for valve type? |  |  |  | Close limit type: Position Torque |
| 13 | Close travel limit set correctly? |  |  |  | Torque limit (if applicable): _________Nm |
| Torque Limits Set-Up |
| 14 | Maximum actuator torque limit set below rated valve gearbox input torque? |  |  |  |  |
|  | - Allowable valve gearbox input torque? |  |  |  | Max. g/b input torque: ____________Nm |
|  | - Opening torque limit setting? |  |  |  | % of Nom.:________ Torque: _______Nm |
|  | - Closing torque limit setting? |  |  |  | % of Nom.:________ Torque: _______Nm |
| Operation |
| 15 | Actuator position indication (% open) correct? |  |  |  |  |
| 16 | Actuator and valve operate smoothly and with uniform speed between 0% and 100% open? |  |  |  |  |
| 17 | Open and close travel limit switches operate correctly during operation? |  |  |  |  |
| 18 | Breakout (unseating) torque during opening acceptable? |  |  |  | Breakout torque: _______________ Nm % of Nom. Torque: _____________ % |
| 19 | Running torque during opening acceptable? |  |  |  | Opening running torque: ________ Nm % of Nom. Torque: _____________ % |
| 20 | Running torque during closing acceptable? |  |  |  | Closing running torque: _________ Nm % of Nom. Torque: _____________ % |
| 21 | Seating torque during closing acceptable? |  |  |  | Seating torque: _______________ Nm % of Nom. Torque: _____________ % |
| 22 | Opening time correct for valve type and size? |  |  |  | Opening time: __________________ |
| 23 | Closing time correct for valve type and size? |  |  |  | Closing time: ____________________ |
| 24 | Valve internals clear of any damage and debris wetted operation? |  |  |  |  |

*Contents of Section 5 to be retained where applicable (e.g. where coating inspection not completed during construction verification). Sections 6 & 7 to be retained in all ITPs.

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that asset external coating is free of damage |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES

| A1. MECHANICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |
|  |  |  |  | ITP-SV-M-VALVE-REGULATING SLEEVE |
|  |  |  |  | ITP-CV-M-VALVE-REGULATING SLEEVE |

APPENDIX A – SITE SPECIFIC PRE-REQUISITES (cont’d)

| A2. ELECTRICAL PRE-REQUISITES | DONE | NO | ITR / DOCUMENT REF. |
| --- | --- | --- | --- |