A) INTRODUCTION

The following procedure is intended to ensure that the quality of constructed product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for all REGULATING VALVE SLEEVE Commissioning personnel shall complete all inspection/commissioning activities and record all activities on Water Corporation Document ITR-SV-M-VALVE-REGULATING-SLEEVE for each asset commissioned.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and AS/NZS Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_SV_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate details match valve specification |  |  |  | Check designations for the following: Size/Model/Pressure Rating/Connection Detail/ |
| 2 | Direction of flow clearly visible on nameplate or valve body? |  |  |  |  |
| 3 | Weight of valve clearly indicated? |  |  |  | Kg: |
| 4 | Critical spares for valve supplied? |  |  |  |  |
| 5 | Inspect valve to ensure equipment is adequately clean |  |  |  |  |
| 6 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| 7 | Confirm that any special tools required to operate the valve have been provided if ordered from the manufacturer |  |  |  |  |
| 8 | Check that flange faces are clean and are free from any defects resulting from corrosion or any other causes |  |  |  |  |
| 9 | Inspect valve to ensure equipment is adequately clean |  |  |  |  |
| MATERIALS AND ARRANGEMENT |
| 10 | Verify construction materials (refer to valve name plate) with specification and relevant drawings |  |  |  |  |
| 11 | Confirm pattern design (oblique, angled or globe) meets specification and relevant drawings |  |  |  |  |
| 12 | Measure face to face length of valve and verify correct length with manufacturer dimensions or general arrangement drawing(s). |  |  |  | Length: Checked against: MF Dimensions / G.A. Dwg |
| 13 | Confirm flange details on name plate match specifications |  |  |  | Flange Aust. Standard/ISO/ANSI/JIS: Flange Type: Flange Size: Flange Class: |
| 14 | Measure pitch circle diameter of valve and verify with specification / relevant Standards |  |  |  | PCD: |
| 15 | Count number of bolt holes and measure bolt hole diameters. Verify number and diameter lengths with specification / relevant Standards |  |  |  | No.: Dia: |
| 16 | Remove inspection covers and check sleeve for roughed surfaces from sleeve galling or binding. |  |  |  | After inspection position valve gate at 5% open and replace covers |
| 17 | Confirm lift jack boot is secure on lift jack and free of defects |  |  |  |  |
| 18 | Confirm seat seal on inlet side of gate is secure and free of defects. Note the valve gate may need to opened such that inspect is possible through covers |  |  |  |  |
| 19 | Confirm vent and drain valves open and close easily |  |  |  |  |
| 20 | Confirm inspection cover davits are free of distortion and hinges are secure |  |  |  |  |
| 21 | Confirm the support leg bases are square to the floor |  |  |  |  |
| ACTUATOR AND GEARBOXES |
| 18 | Inspect gearbox cover plate fasteners and ensure they are tight with zero lubrication leakage. |  |  |  |  |
| 19 | Check that gearbox to actuator mounting plate fasteners are secure. |  |  |  |  |
| 20 | Check that gearbox / handwheel / actuator are located on correct side of valve as per GA drawings * Gearbox location to be determined by viewing the valve from upstream to downstream |  |  |  |  |
| 21 | Locate and verify that actuator name plate details match specification |  |  |  | Check designations for the following: Size/Model/Torque Rating/Voltage PhaseFrequency/RPM/Enclosure NEMA rating/Turns |
| LIFTING, TRANSPORT AND STORAGE |
| 22 | Valve lifting eye bolts fitted and secure with sufficient threads in body? |  |  |  |  |
| 23 | Confirm lifting lugs are free of defects/distortion |  |  |  |  |
| 24 | Inspection/access cover lifting eyebolts (or threads) installed for safe removal of cover plates? |  |  |  |  |
| 25 | Temporary nozzle cover plates and screwed plugs installed? |  |  |  |  |

| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Test certificates received and acceptable - Body/shell hydrostatic test? - Seat hydrostatic test? - Sleeve hydrostatic test? - Coating continuity test? - Kv Flow test? |  |  |  | Attach certificates to this record |
| 2 | Open and close the valve via the handwheel / cap (request for valve key) or electric actuator if installed and ensure seating is correct |  |  |  |  |
| 3 | Open and close the valve. Check that valve opening / closing convention complies with Water Corporation standards (i.e. ACW close, CW open). |  |  |  |  |
| 4 | Confirm position indicator aligns with valve gate opening position. Removal of inspection cover will be required. |  |  |  |  |
| 5 | Confirm gearbox to lift jack drive assembly operates smoothly without discernible noise |  |  |  |  |

| 5. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 6. MECHANICAL SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

| 7. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verify coating system and specification ensuring that product is approved for purpose. Confirm internal coating is potable water approved. |  |  |  |  |
| 2 | Consider if ambient conditions are acceptable for holiday testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing. Surface dry and clean for holiday testing. |  |  |  |  |
| 3 | Check internal coating type and verify in accordance with relevant specification (circle D1: Epoxy Coating on Steel/Cast Iron or state, A1: Surface Preparation. |  |  |  | A1/ D1 / OTHER _____________ |
| 4 | Conduct ²dry film thickness (DFT) measurements in at least 10 locations and record values in tables below. |  |  |  |  |
| 5 | Visually inspect condition of internal and external coating appearance including uniformity, colour and free from runs, sags, and inclusions. |  |  |  |  |
| 6 | Carry out spark test on internal coating in accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V Pass Fail |
| 7 | Carry out spark test on external coating accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V Pass Fail |
| 8 | Valve passes coating condition assessment in accordance with a forementioned tests and inspection. |  |  |  |  |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pre-treatment of Surfaces

2 Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

| 7a. INTERNAL INSPECTION (Microns - DFT) |
| --- |
| NUMBER OF READS (10) | HIGH | LOW | AVERAGE |
| Comments |  |

| 7b. EXTERNAL INSPECTION (Microns - DFT) |
| --- |
| NUMBER OF READS (10) | HIGH | LOW | AVERAGE |
| Comments |  |

| 7c. FLANGE INSPECTION (Microns - DFT) |
| --- |
| NUMBER OF READS (10) | HIGH | LOW | AVERAGE |
| Comments |  |

| 7d. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7e. COATING SIGNOFFS |
| --- |
| SUPPLIER NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. DELIVERY SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |