A) INTRODUCTION

The following procedure is intended to ensure that the quality of constructed product and its associated activities are completed by competent persons and:

- Comply with current and applicable specified requirements (including Corporation specifications / contract terms and conditions, national / international standards, manufacturer’s recommendations and industry best practices.

- Are conducted in a safe and professional manner.

- Provide an audit trail for verification of Quality Assurance and Quality Control compliance.

This procedure is for all ROTARY VALVES used for materials handling at a set volumetric feedrate . Competent personnel shall complete all inspection / construction activities and record all activities on Water Corporation Document ITP-CV-M-ROTARY VALVE for each asset constructed.

NOTE:

- Please ensure that all ITP documents are completed by a competent person and that all Water Corporation SAFETY and operational requirements are to be complied with at all times in relation with Water Corporation and AS/NZS Standards where applicable.

B) COMPLETED DOCUMENTS

Completed documents are to be scanned and saved as a .pdf file in the relevant AQUA folder utilising the following naming convention:

LOCATION - DISCIPLINE - ASSET – ASSET TYPE – VENDOR NAME – DOCUMENT TYPE – P&ID TAG – REVISION NUMBER

E.g. RavenswoodPS_M_Valve_Butterfly_Tyco_CV_1000BV3422_1

The commissioning manager shall coordinate incorporation of completed ITPs in conjunction with the CAMEL.

Feedback on improvements to ITPs should be directed to MESB Mechanical for incorporation into future versions.

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Visually inspect valve installation and verify correct installation as per manufacturer’s recommendations |  |  |  |  |
| 2 | Confirm that valve location is correct as per drawings |  |  |  |  |
| 3 | Verify correct orientation / direction of flow for installed valve |  |  |  |  |
| 4 | For pull out rotary element, ensure surrounding equipment/structures do not impede maintenance tasks |  |  |  |  |
| 5 | Valve support adequate separate to hopper? |  |  |  |  |
| BOLT-UP |
| 6 | Check that mating flanges are flat, clean and free of irregularities |  |  |  |  |
| 7 | Verify gasket material and thickness |  |  |  | Material: CMF EPDM Other _____________________ Thickness: _________________mm |
| 8 | Confirm all bolts installed on valve and that bolt sizes, material and grade are correct |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 9 | Confirm that associated nut grade is correct |  |  |  | Grade: 5 8 Other __________ |
| 10 | Check that valve rotor free turning prior to bolt-up and tightening |  |  |  |  |
| 11 | Confirm correct protrusion of bolt threads past nut |  |  |  | Protrusion: _____________________ |
| 12 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |
| 13 | Verify bolt torque requirements comply with DS-38. Also verify actual bolt torque applied to each bolt is correct |  |  |  | DS38 bolt torque: _____________Nm Actual bolt torque: _____________Nm |
| 14 | Verify that torque wrench / machine used is calibrated |  |  |  | Calibration certificate date: _________ |
| ISOLATING JOINTS (IF REQUIRED FOR DISSIMILAR METALS ISOLATION) |
| 15 | Where the valve body differs to the hopper materials of construction, ensure isolating washers/gaskets are installed |  |  |  |  |

| 4. TEST (Not Applicable) | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that valve internal coating is free of damage if applicable and accessible |  |  |  |  |
| 2 | Check that valve external coating is free of damage |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |