- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |  |
| --- | --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |  |

| 2. INSPECTION PREPARATION |  |
| --- | --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION |  | YES |  | NO |  | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |  |  |
| 1 | Visually inspect screw conveyor installation and verify correct installation as per manufacturer’s recommendations |  |  |  |  |  |  |
| 2 | Confirm that screw conveyor location is correct as per drawings |  |  |  |  |  |  |
| 3 | Verify correct orientation / direction of flow for installed screw conveyor |  |  |  |  |  |  |
| 4 | Screw conveyor support adequate separate to hopper? |  |  |  |  |  |  |
| BOLT-UP |  |  |  |  |  |  |  |
| 5 | For conveyor trough that needs assembly check that mating flanges are flat, clean and free of irregularities |  |  |  |  |  | Note trough sections are normally numbered |
| 6 | Verify gasket material and thickness between trough sections |  |  |  |  |  | Material: CMF EPDM Other _____________________ Thickness: _________________mm |
| 7 | Confirm that bolt sizes, material and grade are correct for assembling of trough, securing gearbox to bell housing and support structure to foundation |  |  |  |  |  | Size: ________ Material: __________ Grade: 4.6 8.8 Other: _______ |
| 8 | Confirm that associated nut grade is correct |  |  |  |  |  | Grade: 5 8 Other __________ |
| 9 | Confirm correct protrusion of bolt threads past nut |  |  |  |  |  | Protrusion: _____________________ |
| 10 | Confirm correct bolt tightening sequence has been followed |  |  |  |  |  |  |
| 11 | Verify that torque wrench / machine used is calibrated |  |  |  |  |  | Calibration certificate date: _________ |
| 12 | For conveyor spiral’s needing welding for assembly, confirm WS-1 is complied with. |  |  |  |  |  | Ensure any welds are coated or passivated (for SS) accordingly. |
| 13 | For conveyors supplied with drive assemblies separate, mount the gearbox to the spirals drive shaft according to manufacturer’s recommendations. |  |  |  |  |  |  |
| 14 | Ensure any transport locks are removed from spiral’s drive shaft |  |  |  |  |  |  |
| 15 | For gland packed seals ensure the gland follower bolts snugged up evenly? |  |  |  |  |  | Avoid excessively tightening the bolts as this may lead to premature failure of seals |
| 16 | Ensure vent plug is mounted on gearbox |  |  |  |  |  |  |
| 17 | Check level of oil in gearbox is acceptable |  |  |  |  |  |  |
| 18 | Ensure support structure is securely fastened to conveyor trough and feet are square to the foundation |  |  |  |  |  |  |

| 4. TEST (Not Applicable) |  | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |

| 5. COATINGS INSPECTION |  | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- | --- |
| 1 | Check that screw conveyor internal coating is free of damage if applicable and accessible |  |  |  |  |
| 2 | Check that screw conveyor external coating is free of damage |  |  |  |  |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |  |  |  |
| --- | --- | --- | --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |