- All ITR documents to be completed & witnessed by competent person/s

- Compliance to be achieved to contract requirements and all latest versions of applicable standards

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate details match valve specification |  |  |  | Pressure Rating/ Size |
| 2 | Confirm valve type correct |  |  |  | Rotary or Linear? |
| 3 | Confirm number of ports correct |  |  |  | No. of ports? |
| 4 | Confirm if Datasheet/ O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| 5 | Check that flange faces or threaded end connections are clean and are free from any defects resulting from corrosion or any other causes |  |  |  |  |
| 6 | What fluid media will pass through the valve |  |  |  | Water/ Air/ Hydraulic Oil |
| MATERIALS AND ARRANGEMENT |
| 7 | Verify construction materials (refer to valve name plate) with specification and suits fluid media/application |  |  |  | Stainless steel construction with nitrile rubber or hydrocarbon resistant diaphragm and seals? |
| 8 | Measure face to face length of valve and verify correct length with manufacturer dimensions or general arrangement drawing(s). |  |  |  | Length: Checked against: MF Dimensions / G.A. Dwg |
| 9 | Confirm flange or end connection details on name plate match specifications |  |  |  | Flange Aust. Standard: Flange/End Connection Type: Flange/End Connection Size: Pressure Class: |
| ELECTRICAL |
| 10 | Confirm voltage is 24 VDC with minimum voltage tolerance of ±10% |  |  |  |  |
| 11 | Confirm coil insulation class is “F” |  |  |  |  |
| 12 | Confirm coils suitable for switching directly from PLC outputs |  |  |  |  |
| 13 | Confirm valve is fail safe |  |  |  |  |
| 14 | Confirm coils are encapsulated type |  |  |  |  |
| 15 | Confirm coil suitable for continuous energisation |  |  |  |  |
| 16 | Check no. of life cycles/duty cycles is suitable |  |  |  |  |
| 17 | Confirm Hazard Area certification is correct |  |  |  |  |
| 18 | Confirm electrical current, power rating, speed of operation and connection type are correct |  |  |  | Current (A) Power (W) Connection Type Speed of Operation (msec) |
| 19 | Confirm protection rating is correct |  |  |  | IP Rating 65 ? |

| 4. TEST (Not Applicable) | PASS | FAIL | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |

| 5. COATINGS INSPECTION (Not applicable) | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |