| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | INSPECTION DATE |
| INSPECTOR NAME: |  |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports. |

| 3. INSPECTION & TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Foundation and Civil works complete? |  |  |  |  |
| 2 | Pump installed in correct location per drawings? |  |  |  |  |
| 3 | Pump and motor direction of rotation correct per drawings? |  |  |  | Direction of rotation: ACW CW (as viewed from drive end) |
| 4 | Pump installed per manufacturer and Water Corporation recommendations? |  |  |  |  |
| SHAFT, BEARINGS AND SEALS |
| 5 | All shaft locking and anti-brinelling devices removed? |  |  |  |  |
| 6 | Bearing end float within tolerance? |  |  |  | Pump bearing float: ___________ mm Motor bearing float: ___________ mm |
| 7 | For pumps fitted with mechanical seals: - Alignment collars removed? - Seals fitted and set correctly? |  |  |  |  |
| 8 | Bearing RTDs fitted? |  |  |  |  |
| 9 | Vibration transducers fitted? |  |  |  |  |
| 10 | Un-used tappings on bearing housing plugged? |  |  |  |  |
| 11 | Vibration transducers fitted? |  |  |  |  |
| LEVELLING AND ALIGNMENT OF PUMP (For Wetwell Service) |
| 12 | Pump and discharge bend aligned and parallel? |  |  |  |  |
| 13 | Guide rail and brackets correctly bolted, tightened and secure? |  |  |  |  |
| 14 | Proper clearances have been provided below the pump? Minimum sump depth provided? |  |  |  |  |
| 15 | Lifting chain is Cromax rated stainless chain and is load rated to double the pump weight? |  |  |  |  |
| 16 | All electric cables properly supported and covered? |  |  |  |  |
| LEVELLING AND ALIGNMENT OF PUMP (For Drywell Service) |
| 17 | Plinth surface roughness acceptable? |  |  |  |  |
| 18 | Foundation bolts size, material and grade correct? |  |  |  | Size: _______ Material:______________ Grade: ___________________________ |
| 19 | Gap between baseframe and top of plinth adequate for grouting? |  |  |  | Gap: ______________ mm |
| 20 | Pump and motor plumb and level? |  |  |  |  |
| 21 | Pump and pipework flanges aligned and parallel? |  |  |  |  |
| 22 | Correct type of grout used for foundation bolts and baseframe? |  |  |  | Bolt grout: ________________________ Baseframe grout:___________________ |
| 23 | Grout flowable, adequately distributed, free of voids and level with top of baseframe? |  |  |  |  |
| 24 | Correct protrusion of foundation bolt threads past nut? |  |  |  |  |
| 25 | Foundation bolts tightened? |  |  |  |  |
| 26 | Axial clearance for thermal expansion and float acceptable? |  |  |  | Axial clearance: ___________ mm |
| 27 | Pump to baseframe bolts tightened? |  |  |  |  |
| VENTS, DRAINS, SEAL AND COOLING WATER |
| 28 | Vent and drain piping and valves fitted and routed to floor drain (if applicable)? |  |  |  |  |
| 29 | Motor cooling system is fitted and installed correctly (if applicable) |  |  |  |  |
| 30 | Un-used tappings on pump casing plugged? |  |  |  |  |
| SUCTION NOZZLE BOLT-UP |
| 31 | Suction pipework correctly supported with zero load on pump nozzle? |  |  |  |  |
| 32 | Mating flanges flat, clean and free of irregularities? |  |  |  |  |
| 33 | Gasket material and thickness correct? |  |  |  | Material: CMF EPDM Other______ Thickness: ____________ mm |
| 34 | Bolt size, material and grade correct? |  |  |  | Size: _______ Material:_____________ Grade: 4.6 8.8 Other_________ |
| 35 | Correct protrusion of bolt threads past nut? |  |  |  |  |
| 36 | Correct bolt tightening sequence followed? |  |  |  |  |
| 37 | Final bolt torques correct? |  |  |  | Torque: __________________ Nm Refer to pump manufacturer’s recommendation. |
| DISCHARGE NOZZLE BOLT-UP |
| 38 | Discharge pipework correctly supported with zero load on pump nozzle? |  |  |  |  |
| 39 | Mating flanges flat, clean and free of irregularities? |  |  |  |  |
| 40 | Gasket material and thickness correct? |  |  |  | Material: CMF EPDM Other______ Thickness: ____________ mm |
| 41 | Bolt size, material and grade correct? |  |  |  | Size: _______ Material:_____________ Grade: 4.6 8.8 Other_________ |
| 42 | Correct protrusion of bolt threads past nut? |  |  |  |  |
| 43 | Correct bolt tightening sequence followed? |  |  |  |  |
| 44 | Final bolt torques correct? |  |  |  | Torque: __________________ Nm Refer to pump manufacturers recommendation. |

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that asset internal coating is free of damage. Areas of focus include suction and discharge nozzle inside corner and tapping locations |  |  |  | Repair if required according to coating manufacturers recommendation |
| 2 | Check that asset external coating is free of damage |  |  |  | Repair if required according to coating manufacturers recommendation |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |