* All Construction Verification documents shall contain the following sections (1 – 2) which capture generic asset information

| 1. REFERENCE INFORMATION |
| --- |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports. |

*Contents of Section 3 (Inspection) and Section 4 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 3. INSPECTION & 4. TESTING | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Pump installed in correct location per drawings? |  |  |  |  |
| 2 | Pump and motor direction of rotation correct per drawings? |  |  |  | Direction of rotation: ACW CW (as viewed from drive end) |
| 3 | Pump installed per manufacturer and Water Corporation recommendations? |  |  |  |  |
| 4 | Confirm that a dismantling joint exists on delivery pipe work to allow removal of pump from sump? |  |  |  |  |
| 5 | Confirm sufficient clearance for sump water to enter pump suction? |  |  |  |  |
| 6 | Confirm cable and floats have sufficient clearance from pump? |  |  |  |  |
| 7 | Confirm winches and cranes are installed correctly and will not impede pump operation? |  |  |  |  |
| 8 | Confirm guide rails and brackets have been installed in correct location and will not impede pump operation? |  |  |  |  |
| SHAFT, BEARINGS AND SEALS |
| 9 | Pump and motor bearings adequately greased? |  |  |  | Note removal of the bearing housing cover maybe required |
| 10 | Un-used tappings on bearing housing plugged? |  |  |  |  |
| LEVELLING AND ALIGNMENT OF PUMPSET |
| 11 | Plinth surface roughness acceptable? |  |  |  |  |
| 12 | Foundation bolts size, material and grade correct? |  |  |  | Size: _______ Material:______________ Grade: ______________________ |
| 13 | Gap between baseframe and top of plinth adequate for grouting? |  |  |  | Gap: ______________ mm |
|  | Pump and motor plumb and level? |  |  |  |  |
| 14 | - Horizontal (eg. pumpset shafts?) |  |  |  |  |
| 15 | - Vertical (eg. nozzle faces) |  |  |  |  |
| 16 | Pump and pipe work flanges aligned and parallel? |  |  |  |  |
| 17 | Correct type of grout used for foundation bolts and baseframe? |  |  |  | Bolt grout: ___________________ Baseframe grout:______________ |
| 18 | Grout flowable, adequately distributed, free of voids and level with top of baseframe? |  |  |  |  |
| 19 | Correct protrusion of foundation bolt threads past nut? |  |  |  |  |
| 20 | Foundation bolts tightened? |  |  |  |  |
| 21 | Pump to baseframe bolts tightened? |  |  |  |  |
| SUCTION NOZZLE BOLT-UP |
| 22 | Mating flanges flat, clean and free of irregularities? |  |  |  |  |
| 23 | Gasket material and thickness correct? |  |  |  | Material: CMF EPDM Other______ Thickness: ____________ mm |
| 24 | Bolt size, material and grade correct? |  |  |  | Size: _______ Material:_____________ Grade: 8.8 Other_________ |
| 25 | Correct protrusion of bolt threads past nut? |  |  |  |  |
| 26 | Correct bolt tightening sequence followed? |  |  |  |  |
| 27 | Final bolt torques correct? |  |  |  | Torque: __________________ Nm Refer to pump manufacturer’s recommendation. |
| DISCHARGE NOZZLE BOLT-UP |
| 28 | Discharge pipework correctly supported with zero load on pump nozzle? |  |  |  |  |
| 29 | Mating flanges flat, clean and free of irregularities? |  |  |  |  |
| 30 | Gasket material and thickness correct? |  |  |  | Material: CMF EPDM Other______ Thickness: ____________ mm |
| 31 | Bolt size, material and grade correct? |  |  |  | Size: _______ Material:_____________ Grade: 8.8 Other_________ |
| 32 | Correct protrusion of bolt threads past nut? |  |  |  |  |
| 33 | Correct bolt tightening sequence followed? |  |  |  |  |
| 34 | Final bolt torques correct? |  |  |  | Torque: __________________ Nm Refer to pump manufacturer’s recommendation. |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6 & 7 to be retained in all ITPs.

| 5. COATINGS INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Check that asset internal coating is free of damage. Areas of focus include suction and discharge nozzle inside corner and tapping locations |  |  |  | Repair if required according to coating manufacturers recommendation |
| 2 | Check that asset external coating is free of damage |  |  |  | Repair if required according to coating manufacturers recommendation |

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |
| 7. SIGNOFFS |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |