| All ITR documents to be completed & witnessed by competent person/s Compliance to be achieved to contract requirements and all latest versions of applicable standards |
| --- |
| 1. REFERENCE INFORMATION |
| INSPECTION DATA | ASSET DATA |
| PROJECT NAME: | MANUFACTURER: |
| LOCATION: | MF SERIAL NO: |
| INSPECTION DATE: | WC FLER / TAG NO: |
| INSPECTOR NAME: | TYPE / MODEL NO / SIZE: |
| PROJECT / CONTRACT NO: | DESIGN CRITERIA: |
| ATTENDEES: |

| 2. INSPECTION PREPARATION |
| --- |
|  | OSH compliance requirements. |
|  | Obtain QA / QC documentation (review outstanding items). |
|  | Relevant Water Corporation standards. |
|  | Relevant Australian Standards. |
|  | Supporting contract documentation / approved drawings. |
|  | Provision of required test equipment. |
|  | Provision of required test reports and certificates; i.e. hydrostatic test, material certificates, etc. |

*Contents of Section 3 (Inspection) and Section 4 (Test) are Asset Specific and shall reflect relevant SPS / Australian Standard(s) where practicable. Entries shall also be worded to reflect the procedures involved in a step-by-step manner; i.e. “Conduct visual inspection and ensure pre-start photographs are taken”, “Extract bearing housing covers to expose bearings and full shaft length”.

| 3. INSPECTION | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| GENERAL |
| 1 | Locate and verify that name plate/label details match specification and contract requirements |  |  |  | Check: Make/Model/Connection size/Serial number/Duty Flow/Duty Head/Speed/Impeller Diam/Seal model/NPSH3@duty/Duty Power/Year of Manufacture |
| 2 | Casting and machined faces free of sharp edges, burrs and defects? |  |  |  |  |
| 3 | Mating faces match marked and dowelled? |  |  |  |  |
| 4 | Confirm if O&M Manuals have been provided (hardcopy / softcopy) |  |  |  | Hardcopy / softcopy? (please circle) |
| MATERIALS AND ARRANGEMENT |
| 5 | Verify construction materials with material certs, specification and relevant drawings |  |  |  | Refer SPS503 for acceptable materials |
| 6 | Confirm whether sump pump can be operated fully and/or partially submerged |  |  |  | Operating mode: |
| 7 | Confirm whether pump maximum speed complies with SPS503 |  |  |  | Maximum speed: rpm |
| 8 | Confirm major dimensions correct per drawing (eg. hold down bolt spacing, shaft centreline and nozzle face positions)? |  |  |  | Attach a copy of the pumpset drawing to this record sheet highlighting on the drawing which dimensions were checked. |
|  | Suction (Inlet) Nozzles |  |  |  |  |
| 9 | - Flange standard correct? |  |  |  | Flange face: FF / RF |
| 10 | - Diameter correct? |  |  |  | Class: |
| 11 | - Pitch circle diameter correct? |  |  |  | PCD: _____________ mm |
| 12 | - Number and diameter of bolt holes correct? |  |  |  | No.:__________ Dia.:__________ mm |
| 13 | - Any additional inlet pipework requested? |  |  |  | Length: |
|  | Discharge (Outlet) Nozzles |  |  |  |  |
| 14 | - Flange standard correct? |  |  |  | Flange face: FF / RF |
| 15 | - Diameter correct? |  |  |  | Class: |
| 16 | - Pitch circle diameter correct? |  |  |  | PCD: _____________ mm |
| 17 | - Number and diameter of bolt holes correct? |  |  |  | No.:__________ Dia.:__________ mm |
| 18 | - Any additional outlet pipework requested? |  |  |  | Length: |
|  | Appurtenances |  |  |  |  |
| 19 | Pump lifting eyes suitably rated and fitted? |  |  |  |  |
| 20 | Confirm whether any pressure gauge tappings were ordered and supplied? |  |  |  |  |
| 21 | Confirm bosses are provided for all tapping points in the pump casing if applicable? |  |  |  |  |
| 22 | Confirm whether any temperature and vibration sensor mounting holes were ordered and supplied? |  |  |  |  |
| 23 | Confirm whether thermistors or bimetallic switches fitted for motor winding protection? |  |  |  |  |
| 24 | Confirm whether mechanical seal chamber includes oil filling and drainage points if applicable? |  |  |  |  |
| 25 | Confirm cable is appropriately insulated according to SPS 503? |  |  |  |  |
| 26 | Confirm whether float switches were ordered and supplied? |  |  |  |  |
| 27 | Confirm whether any winches and chains were ordered and supplied? Chains must comply with SPS503. |  |  |  | Chain size: Chain load rating: |
| 28 | Confirm whether any pump footings, pedestals or stools were ordered and supplied? |  |  |  |  |
| 29 | Confirm whether any standard discharge bends (‘duckfoot’) or suction bends were ordered and supplied? |  |  |  | Size: |
| 30 | Confirm whether any guide rails and brackets were ordered and supplied? |  |  |  | Size: Material: |
| 4. TEST | PASS | FAIL | N/A | COMMENTS/DETAILS |
| 1 | Confirm material certificates are acceptable |  |  |  |  |
| 2 | Confirm rotating element balance certificate meets required grade |  |  |  |  |
| 3 | Confirm hydrostatic test certificates are acceptable against contract and specification requirements |  |  |  |  |
| 4 | Confirm whether NPSHR test required and completed, as specified in SPS 503. |  |  |  |  |

*Contents of Section 5 to be retained where applicable; i.e. if coatings inspection is required. Sections 6-9 to be retained in all ITPs.

| 5. COATINGS INSPECTION (IF APPLICABLE) | YES | NO | N/A | COMMENTS/DETAILS |
| --- | --- | --- | --- | --- |
| 1 | Verified construction materials with specification and relevant drawings |  |  |  | Substrate material: |
| 2 | Review surface pre-treatment and/or preparation procedure (circle D1: Epoxy Coating on Steel/Cast Iron or state Other) |  |  |  | D1 / OTHER _________________ |
| 3 | Verify coating system and specification ensuring that product is approved for purpose |  |  |  |  |
| 4 | Ensure that surface preparation was acceptable and free from contaminants prior to coating/complies to spec Consider dust and spent abrasive, oil and contamination, flash rusting, slag, porosity, weld spatter, sharp edges, free from laminations, free from burrs etc |  |  |  | Class of surface finish (if known): Profile (if known): Coating application (if known): |
| 5 | Consider if conditions acceptable for testing. Surface temperature should be least 3ºC above dew point and relative humidity less than 85 % before testing |  |  |  | Conditions: |
| 6 | Fully cured coating system should be adherent while in their service condition (Method AS/NZS 3894.9) |  |  |  | Failure force (if known): |
| 7 | Assess degree of cure and hardness of coating is acceptable (method AS 3894.4). Allow sufficient drying and curing of the coating prior conducting testing. The length of time shall be obtained from the coating manufacture. |  |  |  | Method used: |
| 8 | Checked that flange faces are clean and are free from any defects resulting from corrosion or any other cause |  |  |  |  |
| 9 | Visually inspect surfaces and ensure is adequately clean and dry prior to testing |  |  |  | Method/chemicals used: |
| 10 | Check internal coating type and verify in accordance with relevant specification (circle D1: Epoxy Coating on Steel/Cast Iron A1 Surface Preperation) |  |  |  | A1 / D1 / OTHER _____________ |
| 11 | Visually inspect condition of internal coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 12 | Check external coating type and verify in accordance with relevant specification (circleD1: Epoxy Coating on Steel/Cast Iron or state, A1 Surface Preperation ) |  |  |  | A1 / D1 / OTHER _____________ |
| 13 | Visually inspect condition of external coating appearance including uniformity, colour and free from any defect that could impair performance and/or appearance of coating. |  |  |  |  |
| 14 | Calibrate thickness tester to standard of uniform and calibrated thickness, covering appropriate range of film thicknesses to be measured |  |  |  | Method/instrument used: |
| 15 | Visually inspect and measure dry film thickness (DFT) in at least 10 locations on coated surfaces. Record values, ensure compliance with spec and record in table below (note that Flange Thickness is not considered acceptable if not within minimum – maximum range) |
| 16 | Ensure coating fully cured prior continuity testing by checking datasheet for required time to full cure or other appropriate test method |  |  |  | Temp/time: Test method: |
| 17 | Calibrate holiday detector (spark tester) electrode with appropriate volt meter which has been laboratory calibrated within the last 2 years to proposed voltage. Record brand and model of spark tester to be used. |  |  |  | Brand/model used: |
| 18 | Carry out spark test on internal coating in accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 19 | Carry out spark test on external coating accordance to AS/NZS 3894.1 Continuity testing of non-conductive coating – High Voltage (brush) method. Specify voltage at which test is carried out. |  |  |  | Test Voltage: V |
| 20 | Asset passes continuity testing with zero defects (including pinholes, holidays, cracks and other discontinuities) detected in finished coating for immersed/buried conditions and/or subsequent repairs have been carried out before being placed in service. |  |  |  |  |

| Coating Thickness: | Internal (micrometers): | External (micrometers): | Flange (micrometers ): |
| --- | --- | --- | --- |
| Specified min |  |  |  |
| Specified max |  |  |  |
| Measured 1 |  |  |  |
| Measured 2 |  |  |  |
| Measured 3 |  |  |  |
| Measured 4 |  |  |  |
| Measured 5 |  |  |  |
| Measured 6 |  |  |  |
| Measured 7 |  |  |  |
| Measured 8 |  |  |  |
| Measured 9 |  |  |  |
| Measured 10 |  |  |  |
| Average |  |  |  |
| Complies with spec | YN | YN | YN |

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pretreatment of Surfaces

2 Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

3 Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

4 Method AS 3894.3 refers Determination of Dry Film Thickness

| 6. REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE | STATUS |
| --- | --- | --- | --- |

| 7. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

POST TRANSPORTATION INSPECTION

- Inspection to be completed at point of delivery

- If a supply verification was not completed at the manufacturer, both supply verification and post transportation inspection should be completed at point of delivery.

| 8. POST TRANSPORTATION REMARKS / REMEDIAL / FOLLOW UP ACTIONS | ACTION BY | TARGET DATE |
| --- | --- | --- |

| 9. SIGNOFFS |
| --- |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |
| NAME (PRINT) | COMPANY / ROLE | SIGNATURE | DATE |

# Footnotes

Refer to AS/NZS 1627 series for Metal Finishing – Preparation and Pretreatment of Surfaces

Refer to AS/NZS 3894.7 for practical procedure for Determination of Surface Temperature of metal surfaced (pre-coating)

Refer to AS/NZS 3894.3 methods for Determination of Dry Film Thickness

Method AS 3894.3 refers Determination of Dry Film Thickness