## L2.1 Heat Shrink Sleeve
INSPECTION AND TEST PLAN Canusa KLON Heat Shrink Sleeve | [12 empty] | Affix Contractor Logo
Project Number: CW |  |  | Project Name: | [9 empty] | Created by: :
Contract Number: |  |  | ITP No: | [5 empty] | Rev: |  |  |  | Approved by:
Package / Lot: |  |  |  | Referenced Codes, Standards and Specifications |  |  | Nomenclature
Scope Description/exclusions: Application of KLON Wrap in Accordance with WC Specification - L2.1 |  |  |  | Referenced Documents: L2.1 DS95 Ver 4 Rev 1 UCC KLON Heat Shrink Sleeve Installation Guide QA10 / QA11 AS4822:2024 Table 6.2 Type 2A-1 |  |  | Control Points |  |  |  | Responsible Position
[7 empty] | H | Hold Point - Formal Invite | R | Review- Check & Sign | PM | Project Manager | SI | Superintendent | SR | Supers Rep
[7 empty] | W | Witness (Formal Invite) | S | Surveillance - Watch Operations | PE | Project Engineer | QI | Quality Inspector
[7 empty] | M | Monitor - Resp for compliance | T | Test by External Party | CM | Construction Manager | SUP | Supervisor | EX | External Party
HOLD POINTS - FORMAL NOTIFICATION REQUIRED - NO WORK IS TO PROCEED UNTIL HOLD RELEASED / WITNESS POINT - FORMAL NOTIFICATION REQUIRED - WORK MAY PROCEED IF NON ATTENDANCE
Item No. | Task / Activity | Frequency | Specified Requirement Reference | Target of Acceptance Pass/Fail Criteria | Evidence / Records | In MDR | Controls and Responsibilities | [5 empty] | Comments / References / Notes
[7 empty] | Sub-Contractor |  | Contractor / Client |  | Water Corporation
[7 empty] | Control | Resp. Sign/Date | Control | Resp. Sign/Date | Control | Sign/Date
1.0 Preliminaries Activities - Approvals and Qualifications
1.1 | Approval Of ITP | AT LEAST 10 DAYS PRIOR TO COMMENCEMENT OF THE ACTIVITY | L2.1 - 4 | The contractor shall submit a proposal for the application of heat shrink sleeve at their factory location and on site. The proposal shall be forwarded to the Corporation for acceptance 10 working days prior to the commencement of work. The proposal shall include an ITP, application procedure and the operator(s) certification. | Release of HOLD Point & Approval to commence This ITP | YES | H |  | H |  | R
1.2 | Submission of qualifications for nominated operators | PRIOR COMMENCEMENT | DS95 - 1.2 DS95 - 14.1.3 | Surface preparation and coating application shall be undertaken by an approved Water Corporation Protective Coating and Concrete Repairs Panel Services member, unless approved otherwise by the Principal. Heat shrink sleeves shall only be installed by accredited and trained applicators. Contractors seeking to use other suppliers of heat shrink sleeves shall seek approval from the Principal. Heat shrink sleeves shall be applied in accordance with Technical Specification L2.1 Heat Shrink Sleeve Requirements. | Current panel member & UCC applicator training and accreditation | YES | M |  | R |  | S |  | UCC provide project specific Applicator Training and Accreditation for all of their Product Solutions, to ensure that the installed product provides the long term performance needed applicators will need to have a UCC accreditation to apply their products.
1.3 | Equipment Calibrations | PRIOR COMMENCEMENT | DS95 - 1.6 DS95 - 14.1.3 | The contractor shall provide all the required inspection equipment necessary to maintain compliance to specification and testing requirements. Spark testing equipment shall be within 2 years of calibration. | Calibration certificates | YES | M |  | R |  | S
2.0 Construction Verification - Manufacturing / Construction / Installation - Process Steps
2.1 | Joint Preparation | ON GOING EACH JOINT | L2.1 - 6.2 Figure 1 | The contractor shall provide a minimum of 100mm cut back on both of the pipe sections proposed to be joined. The edges of the Sintakote® coating shall be bevelled so that there shall be a tapered transition of a minimum of 10mm between the full coating thickness and the exposed steel. | Audit Check Sheet | YES | M |  | S |  | W
2.1 | Joint & Sintakote Preparation | ON GOING EACH JOINT | L2.1 - 6.2 Figure 1 L2.1 6.3 & 6.4 | Verify the edges of the Sintakote® coating have been bevelled so that there shall be a tapered transition of a minimum of 10mm between the full coating thickness and the exposed steel. The heat shrink sleeve will overlap a minimum of 100mm onto the existing Sintakote® coated piping. Where the heat shrink overlaps the Sintakote, light roughing of the Sintakote® surface using a sanding disc or coarse emery paper shall be performed. . | Audit Check Sheet | YES | M |  | R |  | R
2.2 | Surface Preparation | ON GOING EACH JOINT | DS95 - 14.1.3 UCC KLON Heat Shrink Sleeve Installation Guide | The minimum surface preparation requirements shall be mechanical wire brushing/sanding to obtain a St2 cleanliness in accordance with AS/NZS 1627 Part 2. Remove any residual oil/grease contamination with Iso Propyl. Use fresh water to thoroughly clean steel prepared surfaces. | Audit Check Sheet | YES | M |  | R |  | S
2.3 | Verify Number of Heating Torches Required | ONCE UNLESS PIPE OD CHANGES | UCC KLON Heat Shrink Sleeve Installation Guide | Pipe OD: ≤ 600mm (24"): 1 Torch Pipe OD: >600mm (24"): 2 Torches RECOMMENDED Pipe OD: >900mm (36"): 2 Torches MANDATORY Pipe OD: >1830mm (72"): 3 torches MANDATORY. | Audit Check Sheet | NO | M |  | R |  | S |  | It is recommended to use a Gas Torch Kit with 50mm Burner Head.
2.4 | Priming & Profiling | ON GOING EACH JOINT | UCC KLON Heat Shrink Sleeve Installation guide | Apply Primer to all prepared surfaces including welds, step downs and transitions. Allow primer to tack dry Apply Butyl Mastic Strip to All step downs, welds and transitions to ensure the sleeve does not tent or void. | Audit Check Sheet | YES | M |  | R |  | S
2.5 | Pre Heating Joint Area | ON GOING EACH JOINT | L2.1 - heat shrink sleeve requirements UCC KLON Heat Shrink Sleeve Installation Guide | Pre-heat joint area to 40 - 60°C. Verify temperature with a suitable contact probe thermometer, ensuring temperature is correct on the steel at least 150mm (6") on each side of the sleeve. Where the required 40 - 60°C pre-heat cannot be achieved on charged water mains, the cleaned steel and abraded Sintakote to be coated with UCC Protek Butyl (Multi) Primer. Primer to be tack dry before sleeve install commences. | Audit Check Sheet | YES | M |  | R |  | S
2.6 | Installation & Visual Inspection of sleeve | ON GOING EACH JOINT | UCC KLON Heat Shrink Sleeve Installation Guide L2.1 - 7.2 | Install HSS as per UCC KLON installation guide. During shrinking and subsequent cooling check the adhesive shall seep out on both side edges of the sleeve. | Audit Check Sheet | YES | M |  | R |  | S
2.7 | Installer Identification | ON GOING EACH JOINT | UCC KLON Heat Shrink Sleeve Installation guide | Installers shall put the following identifiers on the installed sleeve: 1. Installer initials 2. Certification ID | Audit Check Sheet | YES | M |  | R |  | S
3.0 Defect Identification (Factory/Inspection Release, Punch listing/FTI) / Rectification and Documentation Review & Close-out Activities
3.1 | Holiday test | EACH JOINT ON GOING DURING CONSTRUCTION | DS95 - 14.1.3 & 8.3 | All wrappings and shrink sleeves shall be spark tested by the Contractor ≥ 12 kV using high voltage brush methods to AS 3894.1 prior to backfilling. There shall be no holes, punctures or hollow voids. | Audit Check Sheet | YES | H |  | H |  | S
3.2 | Repairs (If Applicable) | EACH JOINT ON GOING DURING CONSTRUCTION | CRP65 Procedure (IG_NA-CRP65) DS95 - 14.1.3 | Damaged Sintakote pipe coatings and or heat shrink sleeves shall be repaired using the Canusa CRP65 (Coating Repair Patches). | Audit Check Sheet | NO | H |  | W |  | S |  | Crown of pipe repairs can be repaired utilizing Canusa VISCO Wrapidbond where circumferential wrapping is unachievable. Other visco products can be considered with Principal approval.
3.3 | Adhesion test | ONCE A WEEK OR ONE IN EVERY 100 JOINTS | UCC KLON Heat Shrink Sleeve Installation guide. AS4820:2024 Table 6.2 Type 2A-1 CRP65 Procedure (IG_NA-CRP65) | Perform peel test 1. The peeling test for ambient temperature shall be performed at 23±3°C. The temperature shall be measured by a steel (adapted) temperature probe on the sleeve surface. 2. To be performed 1 per week or once per 100 joints (whichever is least frequent). 3. The evaluation length of 100 mm shall be completed within 55 s to 65s. 4. The peel force shall be recorded over a distance of 10mm every 6 s. 5. Following the peel test, coating repair to effected per Installation Guide - CRP65 Repair Patch and UCC Butyl Mastic Filler. | Audit Check Sheet | YES | H |  | W |  | W
3.4 | Final Inspection & Document Review | PRIOR PROJECT COMPLETION | QA10 / QA11 | Approval of Verifying documents, compliance with the Specifications, Standards and Relevant International & Australian Standards | Signed off ITP | YES | H |  | H |  | H
ITP APPROVED & ACCEPTED FOR ISSUE | [8 empty] | ITP Signatory Register
[9 empty] | Name |  |  |  | Signature |  | Initials
SUB-CONTRACTOR |  |  | CONTRACTOR / CLIENT |  | WATER CORPORATION
Name: |  |  | Name: |  | Name:
Signature: |  |  | Signature: |  | Signature:
Date: |  |  | Date: |  | Date: